Issue/Title: Pilgrim Nuclear Power Station (PNPS): Tritium in Groundwater Monitoring Wells

Topic: PNPS Updates as of September 28, 2012

Previous Plans: Results from groundwater monitoring well samples collected during the weeks of July 23, August 6, August 20, and September 3, 2012 were reported by Entergy.  Split sample results for the weeks of July 23, August 6, August 20, and September 3, 2012 were also reported by MERL.

Current Status:

Table 1:  July 23rd 	                               		Table 2:  August 6th

| Location | Date | MERL pCi/L | GEL pCi/L |  | Location | Date | MERL pCi/L | GEL pCi/L |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MW 201 | 07/23/2012 | 2,424 | 2,310 |  | MW 201 | 08/06/2012 | 775 | 616 |
| MW 202 | 07/23/2012 | - | - |  | MW 202 | 08/06/2012 | - | - |
| MW 202 I | 07/23/2012 | - | - |  | MW 202 I | 08/06/2012 | - | - |
| MW 203 | 07/23/2012 | - | - |  | MW 203 | 08/06/2012 | - | - |
| MW 204 | 07/23/2012 | - | - |  | MW 204 | 08/06/2012 | - | - |
| MW 205 | 07/23/2012 | 4,355 | 4,220 |  | MW 205 | 08/06/2012 | 1,555 | 1,180 |
| MW 206 | 07/23/2012 | 473 | 977 |  | MW 206 | 08/06/2012 | 1,543 | 1,480 |
| MW 207 | 07/23/2012 | - | - |  | MW 207 | 08/06/2012 | - | - |
| MW 208-S | 07/23/2012 | - | - |  | MW 208-S | 08/06/2012 | - | - |
| MW 208-I | 07/23/2012 | - | - |  | MW 208-I | 08/06/2012 | - | - |
| MW 209 | 07/23/2012 | 924 | 1,111 |  | MW 209 | 08/06/2012 | 1,140 | 907 |
| MW 210 | 07/23/2012 | - | - |  | MW 210 | 08/06/2012 | - | - |
| MW 211 | 07/23/2012 | 1,163 | 1,310 |  | MW 211 | 08/06/2012 | 1,479 | 826 |
| MW 212 | 07/23/2012 | - | - |  | MW 212 | 08/06/2012 | - | - |
| MW 213 | 07/23/2012 | - | - |  | MW 213 | 08/06/2012 | - | - |
| MW 214 | 07/23/2012 | - | - |  | MW 214 | 08/06/2012 | - | - |
| MW 215 new | 07/23/2012 | 1,064 | 1,230 |  | MW 215 new | 08/06/2012 | 1,496 | 1,210 |
| MW 217 new | 07/23/2012 | 474 | 925 |  | MW 217 new | 08/06/2012 | 836 | 657 |
| MW 3 | 07/23/2012 | - | - |  | MW 3 | 08/06/2012 | - | - |
| MW 4 | 07/23/2012 | - | - |  | MW 4 | 08/06/2012 | - | - |
| SW-boat ramp | 07/23/2012 | - | - |  | SW-boat ramp | 08/06/2012 | - | - |
| SW-intake | 07/23/2012 | NDA(300)* | NDA(419)* |  | SW-intake | 08/06/2012 | NDA(300)* | NDA(398)* |
| * NDA = not detected at less than activity value listed |  |  |  |  |  |  |  |  |
| ** results pending *** well inaccessible - not analyzed this week |  |  |  |  |  |  |  |  |

Table 3:  August 20th 					Table 4:  September 3rd

| Location | Date | MERL pCi/L | GEL pCi/L |  | Location | Date | MERL pCi/L | GEL pCi/L |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MW 201 | 08/20/2012 | 468 | 438 |  | MW 201 | 09/3/2012 | 521 | NDA(448)* |
| MW 202 | 08/20/2012 | 697 | 871 |  | MW 202 | 09/3/2012 | - | - |
| MW 202 I | 08/20/2012 | NDA(300)* | NDA(346)* |  | MW 202 I | 09/3/2012 | - | - |
| MW 203 | 08/20/2012 | NDA(300)* | NDA(347)* |  | MW 203 | 09/3/2012 | - | - |
| MW 204 | 08/20/2012 | NDA(300)* | NDA(341)* |  | MW 204 | 09/3/2012 | - | - |
| MW 205 | 08/20/2012 | 1,749 | 1,670 |  | MW 205 | 09/3/2012 | 1,658 | 1,400 |
| MW 206 | 08/20/2012 | 1,104 | 1,320 |  | MW 206 | 09/3/2012 | 1,094 | 1,080 |
| MW 207 | 08/20/2012 | 448 | 537 |  | MW 207 | 09/3/2012 | - | - |
| MW 208-S | 08/20/2012 | NDA(300)* | NDA(345)* |  | MW 208-S | 09/3/2012 | - | - |
| MW 208-I | 08/20/2012 | NDA(300)* | NDA(354)* |  | MW 208-I | 09/3/2012 | - | - |
| MW 209 | 08/20/2012 | 919 | 696 |  | MW 209 | 09/3/2012 | 892 | 800 |
| MW 210 | 08/20/2012 | NDA(300)* | 738 |  | MW 210 | 09/3/2012 | - | - |
| MW 211 | 08/20/2012 | 1,155 | 866 |  | MW 211 | 09/3/2012 | 1,154 | 951 |
| MW 212 | 08/20/2012 | *** | *** |  | MW 212 | 09/3/2012 | - | - |
| MW 213 | 08/20/2012 | NDA(300)* | NDA(345)* |  | MW 213 | 09/3/2012 | - | - |
| MW 214 | 08/20/2012 | NDA(300)* | NDA(337)* |  | MW 214 | 09/3/2012 | - | - |
| MW 215 new | 08/20/2012 | 1,102 | 1,090 |  | MW 215 new | 09/3/2012 | 1,254 | 831 |
| MW 217 new | 08/20/2012 | 530 | 657 |  | MW 217 new | 09/3/2012 | 556 | 526 |
| MW 3 | 08/20/2012 | NDA(300)* | NDA(347)* |  | MW 3 | 09/3/2012 | - | - |
| MW 4 | 08/20/2012 | 425 | 419 |  | MW 4 | 09/3/2012 | - | - |
| SW-boat ramp | 08/20/2012 | - | - |  | SW-boat ramp | 09/3/2012 | - | - |
| SW-intake | 08/20/2012 | NDA(300)* | NDA(364)* |  | SW-intake | 09/10/2012 | NDA(300)* | NDA(333)* |
| * NDA = not detected at less than activity value listed |  |  |  |  |  |  |  |  |
| ** results pending *** well inaccessible - not analyzed this week |  |  |  |  |  |  |  |  |

The groundwater monitoring results reported by Entergy show MW205 increased to a level of 4,220 pCi/L of tritium detected during the week of July 23rd, decreased to a level of 1,180 pCi/L of tritium detected during the week of August 6th, increased to a level of 1,670 pCi/L of tritium detected during the week of August 20th, and decreased to a level of 1,400 pCi/L of tritium detected during the week of September 3rd.   Entergy results show that MW206 decreased to 977 pCi/L of tritium detected during the week of July 23rd, increased to a level of 1,480 pCi/L of tritium detected during the week of August 6th, decreased to a level 1,320 pCi/L of tritium detected during the week of August 20th, and decreased to a level of 1,080 pCi/L of tritium detected during the week of September 3rd.  With the exception of MW201, results for the other priority wells during the weeks of July 23rd, August 6th, August 20th, and September 3rd were within typical ranges detected since the groundwater monitoring for tritium began (i.e. no detectable tritium to approximately 1,300 pCi/L of tritium detected).  The level of tritium detected in MW201 during the week of July 23rd (2,310 pCi/L) was higher than historically measured in this well (i.e. <1,000 pCi/L).  Tritium results for the sample from MW201 during the weeks of August 6th (616 pCi/L) and August 20th (438 pCi/L) were consistent with historical results and no tritium was detected in the September 3rd sample.  Entergy is evaluating possible reasons for the result from the week of July 23rd.   Tritium results for non-priority wells were within their typical historical ranges (i.e. no detectible tritium to <1000 pCi/L).  It should be noted the MW212 was inaccessible the week of August 20th due to the ongoing construction of the dry cask storage facility access road and was not able to be sampled.  Split sample results from MERL for the weeks of July 23rd, August 6th, August 20th, and September 3rd were generally consistent with Entergy results (see tables above).

Entergy surface water sampling results for the intake canal downstream of MW205 for the weeks of July 23, August 6, August 20, and September 10, 2012 indicated no detectable tritium.  MERL split sample results for surface water also indicated no detectable tritium for samples collected during the weeks of July 23, August 6, August 20, and September 10, 2012.   MDPH will be following up with Entergy to determine why there is no surface water sample result for the boat ramp area that should have been part of the comprehensive sampling round collected the week of August 20th.

MDPH staff conducted a site visit at PNPS on Thursday August 30, 2012 to observe the excavations underway in the vicinity of the main stack drain line.   Excavations continued to visually inspect the main stack drain line and station heating line during the week of September 3rd.  Entergy reported that all sections of the main stack drain line and station heating line appeared intact and Entergy was having engineering take a look at video taken of the pipes to confirm their findings.  Soil samples were also collected at each excavation site at the depth of pipe observation and splits have been sent to MERL for split sample analysis.

Well MW216 was successfully excavated and was installed September 6th located just down gradient of the end of the deep foundation of the reactor and turbine buildings and up gradient of MW206.  Final well development steps were conducted the week of September 10th and a groundwater sample was collected the week of September 17th.  Four consecutive weekly samples will be collected from MW216.   Results will be evaluated and a decision will be made on a future frequency of testing for this well.

Looking Forward:

MDPH will continue to closely follow all investigational activities that are currently underway at PNPS (i.e. well placement, excavation activities, etc.).

PNPS screening level for tritium in groundwater monitoring wells is 3,000 pCi/L, which is 1/10th of the NRC-approved Pilgrim Offsite Dose Calculation Manual standard for tritium in non-drinking water sources. The EPA drinking water standard is 20,000 pCi/L. The nearest drinking water wells are approximately 2.5 miles from the plant.