|  | Commonwealth of Massachusetts Division of Occupational Licensure Office of Public Safety and Inspections Pre-Inspection Checklist - New Elevator Installations & Modernizations Please e-mail form with request for inspection to: elevator.scheduler@mass.gov |
| --- | --- |

This form certifies that elevator State ID:         Permit No:       is in compliance and ready for inspection

Notice: This checklist reflects the most common violations our inspectors encounter when performing an inspection, other violations may appear during inspections. It is suggested that elevator industry personnel have access to a current set of applicable codebooks. The most common industry codebooks are: 524 CMR MA Elevator Regulations 2018 edition; ASME A17.1 Elevator Code 2013 edition; The Massachusetts State Building Code; NFPA #72 Fire Alarm Code and NFPA #70 National Electric Code-2011

Check each box when the item is completed and in compliance. Please note any variances received from the Board of Elevator Regulations including the state ID number.

In the Machine Room

Access to and from the roof and machine room must be by the means of a stairway. When access is over a sloping roof or a roof

with vertical obstructions, a walkway must be provided. Access must be safe and convenient. It is prohibited to allow access to a

machine room to non-authorized personnel per ASME A17.1, 2.7.3.

All non-elevator-related piping and equipment are prohibited from entering or passing through the machine room per 524 CMR

section 35.00: Part 2 section 2.8 and A17.1, 2.8.2

Electrical disconnects must be lockable in the open position and properly located within sight of the elevator devices as outlined

in NFPA #70 Rule 620-51. All disconnects must be properly fused or utilize a non-self resetting circuit breaker. A lockable

disconnect with overcurrent protection is required to be located in the machine room serving the car lighting per NFPA #70 620-

22 and 620-53 Receptacles in the machine room and machinery spaces shall have GFCI protection either by a GFCI-type

receptacle or a GFCI-type circuit breaker per NFPA #70 Rule 620-85. Warning signs shall be posted when there is power from

more than one source per NFPA #70 Rule 620-52-see also 620-91 & 620-51.

Electrical clearances are to be provided and maintained in front of the controller and disconnect at all times. It is interpreted that

machine room doors that swing into the electrical clearance area endanger worker safety and are prohibited unless they meet the

provisions of NFPA #70 Rule 620-5.

Permanent electric lighting shall be provided in all machine rooms and machinery spaces. The illumination shall be not less than

200 1x (19 fc) at the floor level. The light switch is to be located in the machine room and placed near the machine room doorjamb

per ASME A17.1, 2.7.5 and 524 CMR section 35.00: Part 2 section 2.7.5.1. The required lighting shall not be connected to the

load side of a GFCI per NFPA #70 620-23.

All electrical equipment, controllers, and machines are to be properly installed and grounded per NFPA #70 Rule 620-81 and

ASME A17.1, 2.8.1. All electrical conduits are to be properly secured and routed in a workman like manner.  See NFPA #70

rule 620-21.

An "ABC" type fire extinguisher is required to be located in the room per ASME A17.1, 8.6.1.6.5. The fire extinguisher

should be sized for the room dimensions.

Holes around piping and structure penetrations in the machine room are to be properly filled to maintain a fire rated enclosure and

firestopped per NFPA #70 Rule 300-21. All conductors used in raceways and for hoistway door interlock wiring shall be flame-

retardant per NFPA #70 Rule 620-11/Table-13 & 18.

The machine room door is to be self-closing and self-locking per ASME A17.1, 2.7.3.4.

The clear headroom in the machine room shall be not less than 7 feet. Machine rooms are to be vented and/or heated by mechanical or

natural means to ensure proper-operating temperatures of the equipment at all times per 524 CMR section 35.00: Part 2 section 2.7.9.2.

In the Pit Area

For pits greater than 35 inches in depth, a pit ladder is required with a handrail at least 48 inches above the landing. The ladder is

to be non-combustible and located near the jamb side of the hoistway door, the rungs are to have a clearance of not less than 4 1/2

inches, spaced 12 inches apart and not less than 16 inches wide per ASME A17.1, 2.2.4.2. A pit refuge area of not less than

24 inches in height is also required when the car is on a fully compressed buffer per ASME A17.1, 2.4.1 for traction/drum

elevators and (24 inches x 47 inches horizontally x 24 inches high) or (18 inches. x 35 inches horizontally x 41 inches inchs high)

depending on the pit design for hydraulic elevators per ASME A17.1, 3.4.1.

A pit stop switch is to be located adjacent to the pit ladder and about 18 inches above the landing in order to be accessible before

stepping onto the pit ladder. A second pit stop switch is required when the pit exceeds 66" in depth. A light for the pit is to be

located so as to provide adequate lighting for the area per ASME A17.1, 2.2.5.1. The switch is to be near the stop switch. The

light is to be guarded per ASME A17.1, 2.2.5.2. The required lighting shall not be connected to the load side of the GFCI. Per

NFPA #70 Rule 620-24. A GFCI type receptacle is required in pits and on car tops per NFPA #70 Rule 620-85.  A single

receptacle supplying a permanently installed sump pump shall not require GFCI protection per NFPA #70-620-85.

In the Hoistway

All offsets or ledges within the hoistway greater than two inches are to be tapered to not less than 75 degrees per 524 CMR section

35.00: Part 2 section 2.1.6

Top and bottom car and counterweight runby and vertical clearances are required to meet the requirements of ASME A17.1,

2.4 for traction/drum elevators and ASME A17.1, 3.4 for hydraulic elevators. Overhead working clearances must

be provided in the upper end of the hoistway. When the elevator is at extreme travel, a minimum of 43 inch refuge area is

required for traction/drum elevators when the counterweight is on a fully compressed buffer (plus inertia stopping distance

calculation), and a 43-inch refuge area is to be provided for hydraulic elevators (when the stop ring is engaged). The horizontal

area of the refuge space shall be outlined in a contrasting color. A minimum of 24 inches is required over the crosshead for

traction elevators. Beams are not to interfere with these clearances. A minimum of 6 inches of clearance shall remain between the

top of any auxiliary devices on the car-top and the overhead structure when the car is at extreme upward travel (strike point).

Horizontal clearances shall meet ASME A17.1, 2.4.7.1

Operations and Miscellaneous Items

Two-way 24-hour voice communication is to be provided from the elevator car to a location that can take action per ASME A17.1

2.27.1 and previous ASME interpretations.

Fire alarm initiating devices (smoke detectors) must be properly located in the enclosed elevator lobbies and machine rooms.

Either the fire alarm initiating device in the machine room or hoistway shall cause the visual signal in the car to

illuminate intermittently per ASME A17.1 2.27.4.2. Firefighter’s service is not required for LULA elevators, but if

provided, the installation must meet the full provisions of ASME A17.1, 5.2.1.27.

All glass used in construction of the hoistway enclosure must be laminated. The laminated glass must be marked with the proper

ASME Z97.1, 16 CFR Part 1201 or CAN/CGSB-12.1 laminated glass etching on each and every panel per ASME A17.1, 2.1.1.2.

All hoistway/car door restricted opening devices shall be installed per ASME A17.1, 2.14.5.7

Materials used on floor and walls of an elevator car enclosure must adhere to the flame spread and smoke density requirement of

ASME A17.1, 2.14.2. The materials must be certified and tested for their end use configuration including the type of adhesive

used to secure the material. All glass used in the elevator cab must meet the marking requirements of ASME A17.1, 2.14.1.8.

Illumination at the landing sill shall be not less than 10 fc per ASME A17.1, 2.11.10.2. Hoistway door guides and safety

retainers shall conform to ASME A17.1, 2.11.11.

All elevator controllers are required to be "UL" or "CSA" labeled. Hoistway door interlocks are to be certified. All signage

required by 524 CMR; ASME A17.1 and NFPA #70 must be properly installed including the following examples: code data

plates, fire service instructions, emergency identification numbering, hoistway door floor numbers, rope data tags, in-car capacity

tags, crosshead data tags, governor rope data tags, full load working pressures, and governor tripping speeds.

A completed form must be submitted for each inspection requested for new installations and modernizations of passenger, freight, LULA, VRC, wheelchair lift, escalator, etc.

I certify that the following elevator State ID No:        Permit No:       is in compliance and ready for inspection.

Must be completed by an Authorized Representative of Elevator Company Signature: Date: Email: By typing name above you agree that it is valid as your signature.

| Location name |  |  | Address | City | Zip |
| --- | --- | --- | --- | --- | --- |
| Owner/ Authorized Representative |  | Email | Address | City | Zip |
| Elevator Co. |  | Email | Address | City | Zip |

Remarks: