- Public Water System Response to Loss of Pressure to All or Part of the Distribution System

Excerpt from AWWA Standard ANSI/AWWA C651-92 for Disinfecting Water Mains

Section 10: disinfection procedures when cutting into or repairing existing mains

The following procedures apply primarily when existing mains are wholly or partially dewatered. After the appropriate procedures have been completed, the existing main may be returned to service prior to completion of bacteriological testing in order to minimize the time customers are out of water. Leaks or breaks that are repaired with clamping devices while the mains remain full of pressurized water presents little danger of contamination and require no disinfection.

Sec. 10.1 Trench Treatment

When an existing main is opened, either by accident or by design, the excavation will likely be wet and may be badly contaminated from nearby sewers. Liberal quantities of hypochlorite applied to open trench areas will lessen the danger from such pollution. Tablets have the advantage in such a situation because they dissolve slowly and continue to release hypochlorite as water is pumped from the excavation.

Sec. 10.2 Swabbing with Hypochlorite Solution

The interior of all pipe and fittings (particularly couplings and sleeves) used in making the repair shall be swabbed or sprayed with a 1 percent hypochlorite solution before they are installed.

Sec. 10.3 Flushing

Thorough flushing is the most practical means of removing contamination introduced during repairs. If valve and hydrant locations permit, flushing toward the work location from both directions is recommended. Flushing shall be started as soon as the repairs are completed and shall be continued until discolored water is eliminated.

Sec. 10.4 Slug Chlorination

When practical, in addition to the procedures above, the section of main in which the break is located shall be isolated, all service connections shut off, and the section flushed and chlorinated as described in Sec. 5.3, except that the dose may be increased to as much as 300 mg/l and the contact time reduced to as little as 15 min. After chlorination, flushing shall be resumed and continued until discolored water is eliminated, and the water is free of noticeable chlorine odor.

Sec. 10.5 Sampling

Bacteriological samples shall be taken after repairs are completed to provide a record for determining the procedure's effectiveness. If the direction of flow is unknown, then samples shall be taken on each side of the main break. If positive bacteriological samples are recorded, then the situation shall be evaluated by the public water supplier (or public water supplier's representative) who can determine corrective action, and daily sampling shall be continued until two consecutive negative samples are recorded.

Sometimes a public water system may lose pressure as a result of a main repair or accident. The following flow chart may be useful in determining the appropriate steps.