INDOOR AIR QUALITY ASSESSMENT Rita Edwards Miller Elementary School 1 Mitchell Way Westford, Massachusetts 01886 Prepared by: Massachusetts Department of Public Health Bureau of Environmental Health Indoor Air Quality Program December 2009

# Background/Introduction

At the request of the Westford Health Department, the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) conducted an indoor air quality (IAQ) assessment at the Rita Edwards Miller Elementary School (MES) located at 1 Mitchell Way, Westford, Massachusetts.  On September 30, 2009, Michael Feeney, Director of BEH’s IAQ Program visited the school to conduct the assessment.  Mr. Feeney was accompanied by Sharon Lee and Cory Holmes, Environmental Analysts/Inspectors within BEH’s IAQ Program, as well as a school custodian for portions of the assessment.

The MES is a red brick building that was completed in 2003.  The building consists of two, two-story classroom wings that flank a central office area and library in a V-shape.  A third wing to the north connects the classroom wings creating a triangular courtyard.  This third wing contains the cafeteria, music room, boiler plant and gymnasium.  The library and portions of the classroom wings have peaked metal roofs; the remainder of the building has flat rubber membrane roofs.  Windows are openable throughout the building.

Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were conducted with the TSI, Q-Trak, IAQ Monitor, Model 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  Screening for total volatile organic compounds (TVOCs) was conducted using a Thermo Environmental Instruments Inc., Model 580 Series Photo Ionization Detector (PID).  BEH staff also performed visual inspection of building materials for water damage and/or microbial growth.

Results

The school houses approximately 390 kindergarten through second grade students and a staff of approximately 75.  Tests were taken during normal operations at the school and results appear in Table 1.

Discussion

## Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 parts per million (ppm) in all but one area surveyed indicating adequate air exchange throughout the building.  An elevated dioxide level of 1269 in the teacher’s lounge was likely related to a non-operating exhaust ventilation unit in the room.

Mechanical ventilation for classrooms is provided by air-handling units (AHUs) located in penthouse mechanical rooms (Picture 1).  AHUs draw air in through fresh air intakes located on the exterior of the building (Picture 2).  Air is filtered and heated by the AHU before it is distributed by variable air volume boxes to occupied areas via ceiling-mounted air diffusers (Picture 3).  Exhaust air is drawn into the ceiling plenum via grates and returned back to the AHUs via ductwork (Picture 4).  In addition to the aforementioned teacher’s lounge, exhaust ventilation was not operating in some rooms on the first-floor B-wing (Table 1).  It is important to note that in some classrooms, exhaust vents are located above or near hallway doors.  When classroom doors are open, exhaust vents tend to draw air from the hallway, thereby reducing the effectiveness of the vents to remove common environmental pollutants from classrooms.  Doors to these classrooms should remain closed to allow for appropriate removal of air from these rooms.

As mentioned, local airflow to each air diffuser is controlled by a variable air volume (VAV) box.  Each VAV box has a set of thermostat-controlled dampers that open or close to regulate the amount of fresh air provided, depending on the temperature demand for a serviced area.  Thermostats that control the VAV boxes have fan settings of “on” and “automatic”.  The majority of thermostats were set to the fan “auto” setting.  The “automatic” setting on the thermostat activates the HVAC system at a preset temperature.  Once the thermostat detects that the preset temperature has been reached, the VAV box dampers close until heating or cooling is needed.  During times that the temperature of a space is adequate, the VAV box closes its damper and limits the amount of fresh air.  If the thermostat calls for the HVAC system to provide heat, the AHU fresh air intake damper would close to increase the temperature of the air in the ductwork and occupied spaces.  Airflow would be noted from the ceiling air diffusers because the VAV box dampers are open, but fresh air supply would be limited by the closing of the rooftop fresh air intake damper and heated air would be circulated.

While it has the advantage of energy conservation and lower operating costs, VAV box systems may cause problems of insufficient outside air supply particularly if they are set to fan “auto”.  Once the temperature requirement is met, airflow drops.  Airflow can drop to zero in poorly performing HVAC systems (Plog, Niland and Quinlan, 1996).  Consideration should be given to increasing the fresh air supplied to the VAV boxes servicing the ground floor areas to improve ventilation to these areas and operating the thermostats with the fan setting in the “on” position to provide continuous airflow during occupied periods, which is recommended by the MDPH.  Without proper ventilation, normally existing indoor pollutants as well as odors can accumulate, which can lead to complaints.

As discussed, general mechanical ventilation for classrooms is contained in the penthouses.  Based on BEH staff observations, each mechanical penthouse has its own dedicated mechanical system.  A motorized exhaust vent is located next to that of the general HVAC system appears to be two-fold: since the roof of the penthouse appears to lack insulation (Picture 7) nts, despite the presence of filter racks (Picture 6).  The floor of the passive fresh air supply and the ductwork of the general HVAC system is insulated (Picture 8), this penthouse vent system is likely used to remove waste heat in the winter to prevent roof ice dams and also vent exhaust ductwork (Blueprint 1, Picture 5) to draw air out from the penthouse, while a passive fresh air supply vent, located alongside the general HVAC system fresh air supply vent, allows fresh air to enter the interior of the penthouse (Picture 6).  The purpose of this passive supply/motorized exhaust ventilation system excessive heat from building up in the penthouse during hot weather.

According to blueprints made available to IAQ staff, each passive fresh air supply was designed to have a filter installed to prevent outdoor pollutants (e.g., pollen) from entering the penthouse.  No such filters are installed in these ve is coated with accumulated pollen and other debris as well as the floor of the penthouse (Picture 9).  The fresh air supply ducts have holes, which can draw penthouse air and pollutants into the general HVAC system.  In addition, filters for the general HVAC system were stored in each penthouse (Picture 10); storage of filters in this location can allow the media to become coated with pollen and other outdoor pollutants.  Each of these conditions may result in the distribution of pollen and other pollutants into the indoor environmental via the general HVAC system.

Fresh air for common areas such as the gymnasium, cafeteria, library and administrative areas is provided by rooftop AHUs.  The exhaust ventilation for these areas consist of ceiling and wall-mounted exhaust vents connected to rooftop fan units.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of school occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The system was last balanced in 2003.

The Massachusetts Building Code requires that each room have a minimum ventilation rate of 15 cubic feet per minute (cfm) per occupant of fresh outside air or openable windows (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, consult Appendix A.

Indoor temperature measurements ranged from 68º F to 71º F, which were within or slightly below the MDPH recommended comfort range the day of the assessment (Table 1).  The MDPH recommends that indoor air temperatures be maintained in a range of 70o F to 78o F in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.

The relative humidity measured in the building ranged from 41 to 57 percent, within the MDPH recommended comfort range in all areas surveyed during the assessment (Table 1).  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

Microbial/Moisture Concerns

During the course of examining the rooftop penthouses, BEH staff noted evidence of birds, including two dead birds in one penthouse (Picture 11) and bird waste on the floor of all three penthouses (Picture 12), on the floor of each of the rooftop penthouses.  Means for birds to enter the rooftop penthouses include spaces around and within the passive fresh air supply vents for the penthouse vent system (Picture 13 and 14), as evidenced by bird foot prints in the pollen coating the floor of the ductwork.  The possible absence of a bird screen over the openings of the fresh air intake vents allows for easy entry.  It is possible that birds may be present within ductwork connected the fresh air supply vent to the general HVAC system.  This contingency could not be examined due to the absence of visible inspection doors in the fresh air supply ducts in all rooftop penthouses.

Bird wastes in a building raise concerns because of diseases associated with bird wastes.  Certain molds associated with bird waste are of concern, especially for immune-compromised individuals.  Other diseases of the respiratory tract may also result from chronic exposure to bird waste.  Exposure to bird wastes is thought to be associated with the development of hypersensitivity pneumonitis in some individuals.  Psittacosis (bird fancier's disease) is another condition closely associated with exposure to bird wastes in either the occupational or bird raising setting.  While immune-compromised individuals have an increased risk of health impacts following exposure to the materials in bird wastes, these impacts may also occur in healthy individuals exposed to these materials.  Considering the potential health impacts associated with exposure to bird wastes, the need for clean up and appropriate disinfection is critical.

The methods to be employed in clean up of a bird waste problem depend on the amount of waste and the types of materials contaminated.  The MDPH has been involved in several indoor air investigations where bird waste has accumulated within ventilation ductwork (MDPH, 1999).  Accumulation of bird wastes has required clean up of such buildings by a professional cleaning contractor.  In less severe cases, the cleaning of the contaminated material with a solution of sodium hypochlorite has been an effective disinfectant (CDC, 1998).  Disinfection of non-porous materials can be readily accomplished with this material.  Porous items contaminated with bird waste should be examined by a professional restoration contractor to determine if the material is salvageable.  Where a porous material has been colonized with mold, it is recommended that the material be discarded (ACGIH, 1989).

The protection of both the cleaner and other occupants present in the building must be considered as part of the overall remedial plan.  Where cleaning solutions are to be used, the “cleaner” is required to be trained in the use of personal protective methods and equipment (to prevent either the spread of disease from the bird wastes and/or exposure to cleaning chemicals).  In addition, the method used to clean up bird waste may result in the aerosolization of particulates that can spread to occupied areas via openings (doors, etc.) or by the ventilation system.  Methods to prevent the spread of bird waste particulates to occupied areas or ventilation ducts must be employed.  In these instances, the result can be similar to the spread of renovation-generated dusts and odors in occupied areas.  To prevent this, the cleaner should employ the methods listed in the SMACNA Guidelines for Containment of Renovation in Occupied Buildings (SMACNA, 1995).

Several classrooms had water-damaged ceiling tiles which can indicate sources of water penetration from either the building envelope or plumbing system (Pictures 15 and 16; Table 1).  Water-damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired.

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.  Once mold has colonized porous materials, they are difficult to clean and should be removed and discarded.

Plants were noted in several classrooms.  Plants can be a source of pollen and mold which can be respiratory irritants to some individuals.  Plants should be properly maintained and equipped with drip pans and should be located away from univents to prevent the aerosolization of dirt, pollen and mold.

Open seams between sink countertops and walls were observed in some rooms (Picture 17).  If not watertight, water can penetrate through the seam, causing damage.  Improper drainage or sink overflow can lead to water penetration into the countertop, cabinet interiors and areas behind cabinets.  Water penetration and chronic exposure of porous and wood-based materials can cause these materials to swell and show signs of water damage.  Repeated moistening of porous materials can result in mold growth.

A water-stained floor tile was observed in Tutorial 1B (Picture 18).  At the time of the assessment, BEH staff observed that the water bubbler located across from the room was leaking (Picture 19).  Debris in the sink or clogging of the drainage can result in water overflow, resulting in water to spill onto the floor.  Water stains in Tutorial 1B suggests that the floor is pitched slightly towards the room, resulting in water pooling and stains.

Lastly, a humidifier was observed in one classroom (Table 1).  Humidifiers can aerosolize particles and odors.  In addition, the water reservoirs can provide a source for mold growth.  Water reservoirs for humidifiers should be cleaned as per manufacturer’s directions to prevent microbial growth and odors.  The air diffuser should also be cleaned periodically to prevent dust collection and aerosolization of materials.

Point Source Concerns

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor, and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the school environment, BEH staff obtained measurements for carbon monoxide and PM2.5.

### Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  Outdoor carbon monoxide concentrations were non-detect (ND) the day of the assessment (Tables 1).  No measureable levels of carbon monoxide were detected in the building during the assessment (Table 1).

### Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 microgram per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

Outdoor PM2.5 concentrations throughout the day ranged from 1 to 3 μg/m3 (Table 1).  PM2.5 levels measured indoors ranged from 1 to 18 μg/m3 (Table 1), which were well below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur in schools can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, cooking in the cafeteria stoves and microwave ovens; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

### Volatile Organic Compounds

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to determine whether VOCs were present in the building, air monitoring for TVOCs was conducted.  An outdoor air sample was taken for comparison.  Outdoor TVOC concentrations were ND.  Indoor TVOC concentrations were also ND (Table 1).

Please note, TVOC air measurements are only reflective of the indoor air concentrations present at the time of sampling.  Indoor air concentrations can be greatly impacted by the use TVOC containing products.  While no TVOC levels measured exceeded background levels, materials containing VOCs were present in the school.  Several classrooms contained dry erase boards and dry erase board markers.  Materials such as permanent markers, dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.

Cleaning products were also observed in a number of classrooms (Picture 20).  Like dry erase materials, cleaning products contain VOCs and other chemicals.  These chemicals can be irritating to the eyes, nose and throat and should be kept out of reach of students.  Additionally, a Material Safety Data Sheet (MSDS) should be available at a central location for each product in the event of an emergency.  Consideration should be given to providing teaching staff with school issued cleaning products and supplies to prevent any potential for adverse chemical interactions between residues left from cleaners used by the schools facilities staff and those left by cleaners brought in by others.

Air fresheners and deodorizing materials were observed in a number of areas (Picture 20).  Air deodorizers contain chemicals that can be irritating to the eyes, nose and throat of sensitive individuals.  Many air fresheners contain 1,4-dichlorobenzene, a VOC which may cause reductions in lung function (NIH, 2006).  Furthermore, deodorizing agents do not remove materials causing odors, but rather mask odors that may be present in the area.

A laminator and photocopier were observed in Tutorial 1A.  Lamination odors were detected in this room.  Lamination machines melt plastic and give off odors and VOCs.  Similarly, photocopiers also produce VOCs and ozone, particularly if the equipment is older and in frequent use.  Ozone is a respiratory irritant (Schmidt Etkin, 1992).  While this room does have exhaust ventilation, no dedicated exhaust system exists to remove heat and odors produced by this equipment.  Consideration should be given to placing a fan near an open window and operating the fan in a manner that removes laminator odors and heat.

BEH staff observed tennis balls which had been sliced open and placed on chair and/or table legs (Picture 21).  Tennis balls are made of a number of materials that are a source of respiratory irritants.  Constant wearing of tennis balls can produce fibers and cause VOCs to off-gas.  Tennis balls are made with a natural rubber latex bladder, which becomes abraded when used as a chair leg pad.  Use of tennis balls in this manner may introduce latex dust into the school environment.  Some individuals are highly allergic to latex (e.g., spina bifida patients) (SBAA, 2001).  It is recommended that the use of materials containing latex be limited in buildings to reduce the likelihood of symptoms in sensitive individuals (NIOSH, 1997).

### Other Conditions

Other conditions that can affect indoor air quality were observed during the assessment.  In several classrooms, items were observed on the floor, windowsills, tabletops, counters, bookcases and desks.  The large number of items stored in classrooms provides a source for dusts to accumulate.  These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.  In addition, these materials can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

Stuffed pillows/toys and upholstered furniture were noted in some classrooms.  Stuffed toys used by an individual child should be washed on a weekly basis to prevent disease (Hale and Polder, 1996).  Furthermore, stuff pillows/toys can be a point for dust collection.  Close contact with such items can leave oils, perspiration, hair and skin cells.  Dust mites feed upon human skin cells and excrete waste products that contain allergens.  As discussed, dust can be irritating to the eyes, nose and respiratory system.

A number of air diffusers, exhaust vents and personal fans were observed to have accumulated dust/debris (Pictures 22 and 23).  These diffusers, vents and fans should be cleaned in order to prevent dust/debris from being aerosolized and redistributed throughout the room.

Boiler room odors were reported in the music room and its adjoining storage room.  The music storage room abuts the boiler room area.  BEH staff examined the area above the ceiling plenum in the storage room.  Visible light could be seen penetrating through the wall above the plenum, indicating a pathway for odors to migrate from the boiler area to the storage area and music classroom (Picture 24).  Measures to seal this breach (i.e. spray foam) should be considered to prevent future odor occurrences.  Utility holes and breaches in the boiler room should also be sealed (Picture 25).  Additionally, the door to the boiler room was open on the day of assessment (Picture 26); this door should remain closed.

# Conclusions/Recommendations

The conditions observed in the MES are somewhat complex.  Water damaged building materials appear to be the result of ice dams.  Without the means to prevent ice dams, continued water penetration is likely.  In addition, the presence of birds and nesting materials and the lack of bird screens on exterior vents can continue to be potential sources of asthma exacerbation.  In view of the findings at the time of the visit, the following recommendations are provided.

- Remove birds, nesting materials and associated wastes and disinfect attic space.

- Install bird screens on exterior vents.

- Refrain from storing filters in the penthouse.

- Consider examining the interior of ductwork connected to the general HVAC system in the penthouse.

- Operate all ventilation systems throughout the building (e.g., gym, cafeteria, classrooms) continuously during periods of occupancy independent of thermostat control to maximize air exchange.

- Ensure exhaust vents in classrooms on the first floor of the B-wing are operational, make repairs as needed.

- Use openable windows in conjunction with mechanical ventilation to facilitate air exchange.  Care should be taken to ensure windows are properly closed at night and weekends to avoid the freezing of pipes and potential flooding.

- Close classroom doors to facilitate air exchange.

- Consider increasing fresh air supply to VAV boxes.

- Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Install filters to the passive supply system for the penthouse to prevent infiltration of pollen and dusts.

- Repair any existing water leaks and replace any remaining water-damaged ceiling tiles.  Examine the area above these tiles for mold growth. Disinfect areas of water leaks with an appropriate antimicrobial, as needed.

- Ensure plants are equipped with drip pans.  Examine drip pans periodically for mold growth and disinfect with an appropriate antimicrobial, as needed.  Move plants away from fresh air supply sources.

- Seal areas around sinks to prevent water damage to the interior of cabinets and adjacent wallboard.

- Ensure humidifier is cleaned periodically as per manufacturer’s instruction.  If humidifier cannot be maintained, discontinue use.

- Store cleaning products properly and out of reach of students.  All cleaning products used at the facility should be approved by the school department with MSDS’ available at a central location.

- Refrain from using plug-in air fresheners or other air deodorizers.

- Consider opening a window and operating a fan in a manner that removes odors and waste heat when operating the laminator.

- Ensure spaces above the ceiling tile system are sealed in the music storage room to prevent infiltration of boiler room odors.  Ensure the boiler room door remains closed.

- Consider replacing tennis balls with latex-free tennis balls or glides.

- Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms.  Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

- Clean accumulated dust and debris periodically from the surface of air diffusers, exhaust vents and blades of personal and ceiling fans.

- Consider adopting the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good indoor air quality environment in the building.  This document is available at: http://www.epa.gov/iaq/schools/index.html.

- Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://mass.gov/dph/indoor_air.

References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 62-1989

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.   Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

Lstiburek, J. & Brennan, T. 2001.  Read This Before You Design, Build or Renovate.  Building Science Corporation, Westford, MA.  U.S. Department of Housing and Urban Development, Region I, Boston, MA

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

NIH.  2006.  Chemical in Many Air Fresheners May Reduce Lung Function (#06-11). National Institutes of Health, Research Triangle Park, NC.

NIOSH. 1997. NIOSH Alert: Preventing Allergic Reactions to Natural Rubber Latex in the Workplace. National Institute for Occupational Safety and Health, Atlanta, GA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Plog, B., Niland, J. and Quinlan, P., eds. Fundamentals of Industrial Hygiene. 4th ed. Illinois: National Safety Council, 1996.

Sanford. 1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo( Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

SMACNA.  1995. IAQ Guidelines for Occupied Buildings Under Construction.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA.  2001.  “Mold Remediation in Schools and Commercial Buildings”.  Office of Air and Radiation, Indoor Environments Division, Washington, DC.  EPA 402-K-01-001.  March 2001.  Available at: http://www.epa.gov/iaq/molds/mold_remediation.html

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Penthouse  Passive Fresh Air Supply Vent

Penthouse Exhaust Vent

Picture

AHU in penthouse mechanical room

Picture

Fresh air vent to penthouse mechanical room

Picture

Supply vent

Picture

Exhaust vent

Picture

Motorized exhaust vent for penthouse

Picture

Passive fresh air supply vent, note lack of filter and presence of a filter rack  (arrow)

Picture

Roof of the penthouse, note lack of insulation

Picture

General HVAC equipment, note all ducts are insulated

Picture

Accumulate pollen coating the floor of a HVAC penthouse

Picture

Filters for the general HVAC system stored in penthouse

Picture

Dead birds in rooftop HVAC penthouses

Picture

Example of bird waste and nesting materials

Picture

Space around outside of duct coated with bird waste

Picture

Bird foot prints in pollen coating floor of ductwork

Picture

Water-damaged ceiling tile

Picture

Water-damaged ceiling tiles

Picture

Breach between sink backsplash and countertop

Picture

Water stained floor tile, note water bubbler across hall

Picture

Leaking water bubbler across from Tutorial 1B

Picture

Cleaning products and deodorizers

Picture

Tennis balls on chair legs

Picture

Dusty supply vent

Picture

Dusty personal fan

Picture

Ceiling plenum above music storage room, note light penetration

Picture

Utility holes

Picture

Open boiler room door

| Location | Occupants in Room | Temp (°F) | Relative Humidity (%) | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | VOCs (ppm) | PM2.5 (ug/m3) | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Outside/Background: 10:45 AM |  |  |  |  |  |  |  |  |  |  |  |
| Front Entrance |  | 60 | 54 | 376 | 0 | ND | 3 |  |  |  |  |
| 101 |  | 59 | 59 | 352 | 0 | 0 | 1 |  |  |  |  |
| 107/gym |  | 66 | 45 | 348 | 0 | 0 | 1 |  |  |  |  |
| Music |  | 58 | 61 | 361 | 0 | 0 | 2 |  |  |  |  |
| 115/cafeteria |  | 58 | 31 | 352 | 0 | 0 | 2 |  |  |  |  |
| 107 |  | 57 | 46 | 347 | 0 | 0 | 2 |  |  |  |  |
| Outside/Background: 12:00 PM |  |  |  |  |  |  |  |  |  |  |  |
| Front Entrance |  | 64 | 41 | 355 | 0 | 0 | 1 |  |  |  |  |
| 101 |  | 61 | 55 | 335 | 0 | 0 | 1 |  |  |  |  |
| 107/gym |  | 60 | 55 | 336 | 0 | 0 | 1 |  |  |  |  |
| Music |  | 65 | 50 | 344 | 0 | 0 | 1 |  |  |  |  |
| 115/cafeteria |  | 63 | 50 | 341 | 0 | 0 | 1 |  |  |  |  |
| 107 |  | 63 | 48 | 346 | 0 | 0 | 1 |  |  |  |  |
| Outside/Background: 1:45 PM |  |  |  |  |  |  |  |  |  |  |  |
| Front Entrance |  | 63 | 40 | 344 | 0 | 0 | 1 |  |  |  |  |
| 101 |  | 61 | 48 | 337 | 0 | 0 | 1 |  |  |  |  |
| 107/gym |  | 59 | 55 | 338 | 0 | 0 | 2 |  |  |  |  |
| Music |  | 59 | 52 | 347 | 0 | 0 | 1 |  |  |  |  |
| 115/cafeteria |  | 60 | 51 | 342 | 0 | 0 | 2 |  |  |  |  |
| 107 |  | 59 | 51 | 339 | 0 | 0 | 2 |  |  |  |  |
| Indoors: |  |  |  |  |  |  |  |  |  |  |  |
| 213 | 1 | 68 | 51 | 585 | 0 | 0 | 6 | Y | Y | Y | DEM, CPs, DO, auxiliary exhaust in bathroom |
| 212 | 5 | 69 | 48 | 502 | 0 | 0 | 2 | Y | Y | Y | DO, DEM, PF, stuffed animals |
| 211 | 0 | 68 | 47 | 435 | 0 | 0 | 1 | Y | Y | Y | DO, DEM, items |
| 210 | 6 | 69 | 48 | 560 | 0 | 0 | 2 | Y | Y | Y | PF, humidifier, TB, 3 WD-CT, stuffed animals, DEM, DEM odors |
| 209 | 18 | 71 | 41 | 489 | 0 | 0 | 1 | Y | Y Dusty | Y Dusty | DO, 25 computers, CPs, 1 WD-CT, DEM, reported as too cold |
| 208 | 3 | 68 | 48 | 501 | 0 | 0 | 1 | Y | Y | Y | 1 WD-CT, breach between sink and backsplash |
| Library | 21 | 68 | 46 | 433 | 0 | 0 | 2 | N | Y | Y |  |
| Guidance | 2 | 68 | 47 | 522 | 0 | 0 | 2 | Y 2/2 open | Y | Y Above door | DO, couch |
| Testing 2 | 0 | 69 | 48 | 546 | 0 | 0 | 2 | Y | Y | Y Above door | DO, DEM, breach between sink countertop and backsplash |
| 201 | 15 | 70 | 45 | 566 | 0 | 0 | 2 | Y | Y | Y | TB, cleaners, DEM, PF, microwave |
| 203 | 19 | 71 | 45 | 690 | 0 | 0 | 5 | Y | Y | Y | DO, PF, TB, cleaners, DEM |
| 200 | 19 | 71 | 45 | 731 | 0 | 0 | 3 | Y | Y | Y | TB, plants, PF - dusty, DEM, 2 WD-CT, breach between sink countertop and backsplash |
| 202 | 19 | 71 | 43 | 682 | 0 | 0 | 2 | Y | Y | Y | 2 WD-CT, TB, CPs, stuffed animals, PF |
| Tutorial 2 | 0 | 71 | 42 | 542 | 0 | 0 | 3 | Y | Y | Y | 4 WD-CT, PF, DO, DEM |
| storage |  |  |  |  |  |  |  |  |  |  | 1 WD-CT, missing light cover, unlabeled bottle, WD-CT in hallway outside of storage room |
| 205 | 22 | 71 | 44 | 762 | 0 | 0 | 4 | Y | Y Dusty | Y | TB, CPs, pillows, DEM, 5 WD-CTs along window |
| 204 | 21 | 71 | 42 | 528 | 0 | 0 | 2 | Y | Y Dusty | Y | DO, PF, DEM, CPs |
| 207 | 21 | 71 | 42 | 651 | 0 | 0 | 4 | Y | Y Dust | Y | DO, TB, CPs, DEM, 1 WD-CT |
| 206 |  |  |  |  |  |  |  |  |  |  | PF, CPs, items, DEM, 6 WD-CT |
| Admin 7 | 0 | 71 | 42 | 471 | 0 | 0 | 1 | N | Y | Y | DO |
| 109 | 2 | 71 | 42 | 474 | 0 | 0 | 2 | Y | Y | Y | DO, DEM, PC |
| Guidance 1 | 0 | 71 | 44 | 442 | 0 | 0 | 1 | Y | Y | Y | DO |
| Nurse’s office | 0 | 70 | 43 | 483 | 0 | 0 | 2 | N | Y | Y | 2 WD-CT |
| Gym | 0 | 70 | 48 | 576 | 0 | 0 | 6 | N | Y | Y |  |
| 118 (teachers’ lounge) | 6 | 70 | 57 | 1269 | 0 | 0 | 18 | Y | Y | Y Off | CPs, soda machine, microwave |
| Cafeteria | 50 | 70 | 49 | 603 | 0 | 0 | 4 | Y | Y | Y | Exterior DO, ~100 students left 5 mins prior |
| 115 | 9 | 69 | 46 | 492 | 0 | 0 | 3 | Y | Y | Y | DO, DEM, CPs, 1 WD-CT |
| 114 | 0 | 69 | 45 | 433 | 0 | 0 | 3 | Y | Y | Y | DO, DEM, 4 WD-CT (room used sparingly) |
| 101 | 21 | 70 | 45 | 586 | 0 | 0 | 3 | Y | Y | Y Off | DEM, breach between sink countertop and backsplash |
| 103 | 1 | 71 | 42 | 483 | 0 | 0 | 2 | Y | Y | Y Off | DO, TB, PF, CPs, CP odors |
| 102 | 19 | 71 | 43 | 612 | 0 | 0 | 2 | Y | Y | Y Off | DO, CPs, breach between sink countertop and backsplash |
| 100 | 20 | 71 | 44 | 640 | 0 | 0 | 3 | Y | Y | Y Off | DO, DEM, CPs, breach between sink countertop and backsplash |
| Tutorial 1A | 3 | 71 | 42 | 480 | 0 | 0 | 2 | Y | Y | Y | DO, PC, laminator - odors |
| 105 | 0 | 71 | 40 | 420 | 0 | 0 | 3 | Y | Y | Y | DO, TB, CPs |
| 107 | 19 | 71 | 43 | 639 | 0 | 0 | 4 | Y | Y | Y | DO, PF, pillows, DEM |
| 106 | 1 | 71 | 43 | 529 | 0 | 0 | 4 | Y | Y | Y | DO, DEM, breach between backsplash and sink countertop, appox 19 students exiting room |
| 104 | 22 | 71 | 44 | 692 | 0 | 0 | 9 | Y | Y | Y | DO, TB, PF, DEM, CPs |
| Music | 22 | 71 | 44 | 582 | 0 | 0 | 3 | Y | Y | Y | DEM, boiler odors from storage room |
| Tutorial 1B | 1 | 69 | 45 | 502 | 0 | 0 | 2 | Y | Y | Y | DO, 1 WD-CT, DEM, water stained floor tile from bubbler |
| 113 | 18 | 70 | 48 | 649 | 0 | 0 | 4 | Y | Y | Y | DEM, CPs, breach between backsplash and sink countertop, items |
| 111 | 20 | 70 | 45 | 630 | 0 | 0 | 4 | Y | Y | Y | DO, TB, CPs, DEM |
| 112 | 14 | 71 | 46 | 673 | 0 | 0 | 4 | Y | Y | Y | CPs, TB, DEM |
| 110 | 14 | 71 | 44 | 635 | 0 | 0 | 5 | Y | Y | Y | PF, TB, CPs, PF |
| 108 | 20 | 72 | 42 | 670 | 0 | 0 | 3 | Y | Y | Y | breach between backsplash and sink countertop, CPs, DEM |