| UST Owner/Operator Requirements: - All cathodic testing must be performed by a cathodic protection tester certified by: NACE, The Steel Tank Institute, or the International Code Council. - Sacrificial – Galvanic cathodic protection systems shall be tested at the following frequency: Standard; Testing Frequency. Test results indicate at least -0.90 volts, or passes the 100-mV Cathodic Polarization Test (NACE Standard TM0101-2012 (tank) and/or TM0497-2012 (Piping)).; Three year intervals.. Test results indicate between -0.85 - -0.90 volts.; Annually. Test results indicate less than -0.85 volts or fails the 100-mV Cathodic Polarization Test (NACE Standard TM0101-2012 (Tank) and/or TM0497-2012 (Piping)).; System is deemed inadequate and unless the system is repaired by the certified cathodic tester and retested with a passing test result within 5 days of the failed test, the O/O shall retain a corrosion expert to determine the cause of the failed test and repair or replace the system within 120 days of the date of the failed test.. - Repaired systems shall be retested within 60 days following repair or excavation at the UST system. - If repairs are not completed within 120 days of the date of the failed test, the UST system shall be taken temporarily out of service, removed or closed in-place, if applicable. - All records in a hard copy or electronic log shall be maintained for a minimum of four years, including corrosion expert’s determination of cause of system failure. |
| --- |
| Facility Name |  |  |  |  | UST ID# |  |
| Cathodic Protection System Test Date: |  |  |  |  |  |  |
| Voltage Testing Result | Volts | TM0101-2012 (Tank) |  | Pass | Fail | NA |
|  |  | TM0497-2012 (Piping) |  | Pass | Fail | NA |
| If voltage testing result is <-0.85 volts, or one or more failed tank or piping cathodic protection tests, date system repaired or replaced: |  |  |  |  |  |  |
| Date retested for repaired or replaced cathodic protection system: |  |  |  |  |  |  |
| Cathodic Protection System Test Date: |  |  |  |  |  |  |
| Voltage Testing Result | Volts | TM0101-2012 (Tank) |  | Pass | Fail | NA |
|  |  | TM0497-2012 (Piping) |  | Pass | Fail | NA |
| If voltage testing result is <-0.85 volts, or one or more failed tank or piping cathodic protection tests, date system repaired or replaced: |  |  |  |  |  |  |
| Date retested for repaired or replaced cathodic protection system: |  |  |  |  |  |  |