|  | Commonwealth of Massachusetts City/Town of Septic System Installation Checklist |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | DEP has provided this form for use by local Boards of Health if they wish to do so. |  |  |  |  |  |  |  |  |  |
|  | A. Applicant Information |  |  |  |  |  |  |  |  |  |
| Important: When filling out forms on the computer, use only the tab key to move your cursor - do not use the return key. | Name |  |  |  |  |  |  |  |  |  |
|  | Address |  |  |  |  |  |  |  |  |  |
|  | City |  |  |  |  | State |  | Zip Code |  |  |
|  | Disposal System Construction Permit # |  |  |  |  | Map |  | Lot |  |  |
|  | Installer |  |  |  |  |  |  |  |  |  |
|  | Designer |  |  |  |  |  |  |  |  |  |
|  | Board of Health Representative |  |  |  |  |  |  |  |  |  |
|  | Inspection Dates: |  |  |  |  |  |  |  |  |  |
|  | Tank: |  | Date |  |  | Leach Area: |  | Date |  |  |
|  | Final: |  | Date |  |  | Other: |  | Date |  |  |
|  | B. Application Checklist |  |  |  |  |  |  |  |  |  |
|  | 1. Pre-Construction Conference |  |  |  |  |  | Approved |  | N/A | Problem |
|  | Sieve analysis supplied for sand |  |  |  |  |  |  |  |  |  |
|  | Current approved plans (3 copies) |  |  |  |  |  |  |  |  |  |
|  | System staked prior to construction |  |  |  |  |  |  |  |  |  |
|  | On-site check for tank water-tightness |  |  |  |  |  |  |  |  |  |
|  | Abandonment of existing system (repairs) |  |  |  |  |  |  |  |  |  |
|  | Plan revision(s) |  |  |  |  |  |  |  |  |  |
|  | Conditions/Approvals |  |  |  |  |  |  |  |  |  |
|  | O/M Plan on file |  |  |  |  |  |  |  |  |  |
|  | DEP approval on file |  |  |  |  |  |  |  |  |  |
|  | B. Application Checklist (cont.) |  |  |  |  |  |  |  |  |  |
|  | 2. Construction Inspection |  |  |  |  |  |  |  |  |  |
|  | a) Building Sewer (310 CMR 15.222) |  |  |  |  |  | Approved |  | N/A | Problem |
|  | All waste pipes tied into building sewer |  |  |  | Basement check |  |  |  |  |  |
|  | Schedule 40 PVC 4” or cast iron |  |  |  | Verify by reading pipe |  |  |  |  |  |
|  | Minimum slope of 0.01-0.02 |  |  |  | Visual |  |  |  |  |  |
|  | Pipe laid in continuous straight line |  |  |  | Visual |  |  |  |  |  |
|  | Pipe laid on compact, firm base |  |  |  | Visual |  |  |  |  |  |
|  | Cleanouts precede all changes in alignment/grade |  |  |  | Verify by visual/tape |  |  |  |  |  |
|  | Cleanout provided every 100 ft. |  |  |  | Verify by visual/tape |  |  |  |  |  |
|  | Backfill material clean |  |  |  | Visual |  |  |  |  |  |
|  | b) Septic Tank (310 CMR 15.223) |  |  |  |  |  | Approved |  | N/A | Problem |
|  | Tank is set level with 6” stone under (15.228) |  |  |  | Check with level |  |  |  |  |  |
|  | Tank is required size/loading per plan |  |  |  | Verify with plan |  |  |  |  |  |
|  | Inlet and outlet are at proper location (15.227) |  |  |  | Verify with plan |  |  |  |  |  |
|  | Tank is water tight (15.226) |  |  |  | Test |  |  |  |  |  |
|  | Outlet tees extend 6” above flow line |  |  |  | Verify by visual/tape |  |  |  |  |  |
|  | Approved filter device placed at outlet |  |  |  | DEP list |  |  |  |  |  |
|  | Gas baffle installed at outlet tee |  |  |  | Visual |  |  |  |  |  |
|  | Inlet and outlet tees on center line |  |  |  | Visual |  |  |  |  |  |
|  | Tank is backfilled with acceptable material |  |  |  | Visual |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |
|  | B. Application Checklist (cont.) |  |  |  |  |  |  |  |  |  |
|  | c) Distribution Box (310 CMR 15.232) |  |  |  |  |  | Approved |  | N/A | Problem |
|  | All outlet pipes at same elevation |  |  |  | Check by adding water |  |  |  |  |  |
|  | Number of outlets | per plan |  |  | Number of laterals |  | per plan |  |  |  |
|  | Inlet tee min. 1” over outlet |  |  |  | Visual and w/tape |  |  |  |  |  |
|  | D box set on level base |  |  |  | Visual |  |  |  |  |  |
|  | Top of D box 36” max depth |  |  |  | Visual and w/tape |  |  |  |  |  |
|  | D box is water-tight |  |  |  | Add water |  |  |  |  |  |
|  | D box has a minimum of 2” thick wall and 12” inside dimension |  |  |  |  |  |  |  |  |  |
|  | d) Pump Chamber (310 CMR 15.231) |  |  |  |  |  | Approved |  | N/A | Problem |
|  | Tank is set level |  |  |  | Visual and w/level |  |  |  |  |  |
|  | Proper volume is provided |  |  |  | Check plan and tank |  |  |  |  |  |
|  | Float elevations set per plan |  |  |  | Measure w/tape |  |  |  |  |  |
|  | Min. 2” delivery line to D box |  |  |  | Visual |  |  |  |  |  |
|  | Number of pumps: |  |  |  |  |  |  |  |  |  |
|  | Specified pump provided or designers approval for equal pump |  |  |  |  |  |  |  |  |  |
|  | Correct pump sequence |  |  |  |  |  |  |  |  |  |
|  | Covers set to grade |  |  |  |  |  |  |  |  |  |
|  | Electrical permit provided |  |  |  |  |  |  |  |  |  |
|  | 6” of stone beneath chamber |  |  |  | Visual |  |  |  |  |  |
|  | Chamber is water-tight |  |  |  | Test |  |  |  |  |  |
|  | Min. 9” cover provided |  |  |  | Visual |  |  |  |  |  |
|  | Correct loading provided per plan |  |  |  | Visual on tank |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |
|  | B. Application Checklist (cont.) |  |  |  |  |  |  |  |  |  |
|  | e) Leaching Facility (310 CMR 15.240) |  |  |  |  |  | Approved |  | N/A | Problem |
|  | No frozen material used including back fill |  |  |  | Visual |  |  |  |  |  |
|  | No clay, tailings or stones larger than 6” for cover material |  |  |  |  |  |  |  |  |  |
|  | Soil at bottom/sides of excavation matches info on deep holes |  |  |  |  |  |  |  |  |  |
|  | All impervious layers removed |  |  |  | Visual |  |  |  |  |  |
|  | No remaining A/B horizons |  |  |  | Visual |  |  |  |  |  |
|  | Groundwater conditions match plan and deep holes |  |  |  | Visual/check plan |  |  |  |  |  |
|  | Vented if under impervious cover per plan (15.241) |  |  |  |  |  |  |  |  |  |
|  | Vent is protected from precipitation and animal entry |  |  |  |  |  |  |  |  |  |
|  | Cover of a minimum of 9” over leach area |  |  |  |  |  |  |  |  |  |
|  | Pipe slope equal to 0.005 |  |  |  | Check w/transit |  |  |  |  |  |
|  | Leach area per design (15.241) |  |  |  |  |  |  |  |  |  |
|  | Excavation is level and at required depth |  |  |  | Visual/check plan |  |  |  |  |  |
|  | Removal of 5 ft material and replacement (if in fill) |  |  |  | Visual/check plan |  |  |  |  |  |
|  | Back fill material is acceptable |  |  |  | Visual |  |  |  |  |  |
|  | Final contours correct per plan |  |  |  | Check with plan |  |  |  |  |  |
|  | Surface/subsurface drainage away from leach area |  |  |  |  |  |  |  |  |  |
|  | Final grade and side slopes are stable |  |  |  |  |  |  |  |  |  |
|  | Distribution lines are capped, vented, or connected together |  |  |  |  |  |  |  |  |  |
|  | Impermeable barrier (15.255[2]) |  |  |  |  |  |  |  |  |  |
|  | Retaining wall inspected by PE |  |  |  |  |  |  |  |  |  |
|  | Retaining wall is water-proofed |  |  |  |  |  |  |  |  |  |
|  | Retaining wall/barrier is at correct depth/height |  |  |  |  |  |  |  |  |  |
|  | B. Application Checklist (cont.) |  |  |  |  |  |  |  |  |  |
|  | f) Leaching trenches (310 CMR 15.251) |  |  |  |  |  | Approved |  | N/A | Problem |
|  | Number of trenches: |  |  |  |  |  |  |  |  |  |
|  | Depth of trenches: |  |  |  |  |  |  |  |  |  |
|  | Width of trenches: |  |  |  |  |  |  |  |  |  |
|  | Trench spacing per plan |  |  |  |  |  |  |  |  |  |
|  | Stone is double-washed [3/4” to 1½”] (15.247) |  |  |  |  |  |  |  |  |  |
|  | g) Leaching fields (310 CMR 15.242) |  |  |  |  |  |  |  |  |  |
|  | Length of field: |  |  |  |  |  |  |  |  |  |
|  | Width of field: |  |  |  |  |  |  |  |  |  |
|  | Min. of 2 distribution lines |  |  |  |  |  |  |  |  |  |
|  | Separation distance conforms to plan |  |  |  |  |  |  |  |  |  |
|  | Stone is double-washed [3/4” to 1½”] (15.247) |  |  |  |  |  |  |  |  |  |
|  | h) Leaching Pits (310 CMR 15.253) |  |  |  |  |  |  |  |  |  |
|  | Number of pits: |  |  |  |  |  |  |  |  |  |
|  | Depth of pits: |  |  |  |  |  |  |  |  |  |
|  | Stone is double-washed [3/4” to 1½”] (15.247) |  |  |  |  |  |  |  |  |  |
|  | Each pit has min. 1 20” access cover |  |  |  |  |  |  |  |  |  |
|  | Piping network and configuration of pits/chambers per plan |  |  |  |  |  |  |  |  |  |
|  | i) Tight Tank (310 CMR 15.260) |  |  |  |  |  |  |  |  |  |
|  | Tank is set level with 6” stone under |  |  |  | Visual and with level |  |  |  |  |  |
|  | Tank is proper size per plan |  |  |  | Visual with plan |  |  |  |  |  |
|  | Pumping contract has been provided |  |  |  |  |  |  |  |  |  |
|  | Covers to grade |  |  |  | Visual |  |  |  |  |  |
|  | A/V alarm set at 3/5 tank capacity |  |  |  | Check floats by raising |  |  |  |  |  |
|  | A/V alarm test on separate circuit |  |  |  | Set off alarm |  |  |  |  |  |
|  | B. Application Checklist (cont.) |  |  |  |  |  |  |  |  |  |
|  | j) Certificate of Compliance (310 CMR 15.021) |  |  |  |  |  |  |  |  |  |
|  | As Built Plan Submitted |  |  |  | Date |  |  |  |  |  |
|  | Signed by Installer |  |  |  | Date |  |  |  |  |  |
|  | Signed by Designer |  |  |  | Date |  |  |  |  |  |
|  | Certificate of Compliance Issued |  |  |  | Date |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |