## Sheet1
MASS/DEPARTMENT OF PUBLIC HEALTH DAILY FLUORIDATION REPORT
Month of | December |  | Year | 2006 | Page | 1 | of | 1 | (Use the same form daily for one month for each source or manifolded or combined sources)
Section I. PWS INFORMATION:
1. PWS Name: |  | Riverdale Water Department | [6 empty] | 2. PWS ID# : | 9999000 |  |  | 3. City/Town or District: |  |  |  | Riverdale, MA
4. Source(s) Fluoridated/MassDEP Source Code/Location ID: | [9 empty] | -01FW
5. Is the Source(s) Manifold? |  |  |  | Yes |  | No | X | [10 empty] | List location or Mass DEP location ID# for the daily sample: | WTP Finished Water
Section II. PWS CHEMICAL USE INFORMATION:
1. Type of fluoride chemical used: |  |  |  |  | NaF | X |  | Na2SiF6 |  |  | H2SiF6
2. What is the purity of the fluoride chemical? | [6 empty] | 99 |  | % (From shipping container or hydrometer test rounded to nearest unit).
3. Are all fluoride-metering pumps protected by two (2) operating anti-siphon (back-pressure) valves? | [16 empty] | Yes | X | No
4. Was each anti-siphon valve disassembled and inspected in the last 12 months? | [12 empty] | Yes | X | Date: | 2006-01-23 |  | No
Expain:
5. Was the fluoride test meter calibrated each day before use? (See Note 2) | [12 empty] | Yes | X | No
Expain:
6. Do you require on site technical assistance? | [6 empty] | Yes |  | No | X |  |  | If yes, explain:
Section III. DAILY RESULT:
[7 empty] | TRUE | FALSE
Days of the Month | Gallons of Water Treated (to the nearest 1,000 gallons) |  |  |  | Amt. Fluoride Added (Lbs) |  | Saturator1 Volume of Make Up Water Added |  |  | Calculated Fluoride Ion Dosage (ppm) |  |  | Results of Fluoride Tests by PWS (ppm) 2,3 |  |  | Name of tester and Comments E.g. Reason(s) for not fluoridating or sampling. Changes in product or batch mixing day etc. | [5 empty] | FALSE
1 | 878000 | [5 empty] | 54 |  |  | 1.212 |  |  | 1.1 |  |  | DS
2 | 978000 | [5 empty] | 74 |  |  | 1.468 |  |  | 1.3 |  |  | SN
3 | 2080000 | [5 empty] | 133 |  |  | 1.2561 |  |  | 1.1 |  |  | TM
4 | 1698000 |  |  |  | 50 |  | 100 |  |  | 1.1648 |  |  | 1 |  |  | SN
5 | 1353000 | [5 empty] | 84 |  |  | 1.2225 |  |  | 1.1 |  |  | DS
6 | 674000 |  |  |  | 50 |  | 36 |  |  | 1.0657 |  |  | 1.1 |  |  | DS
7 | 975000 | [5 empty] | 58 |  |  | 1.1755 |  |  | 1 |  |  | SN
8 | 1180000 | [5 empty] | 78 |  |  | 1.2951 |  |  | 1.2 |  |  | TM
9 | 904000 |  |  |  | 50 |  | 64 |  |  | 1.38 |  |  | 1.2 |  |  | SN
10 | 1865000 | [5 empty] | 112 |  |  | 1.1858 |  |  | 1.1 |  |  | DS
11 | 1953000 |  |  |  | 50 |  | 128 |  |  | 1.285 |  |  | 1 |  |  | DS
12 | 695000 | [5 empty] | 35 |  |  | 1.0105 |  |  | 1.1 |  |  | DS
13 | 753000 | [5 empty] | 48 |  |  | 1.2525 |  |  | 1.1 |  |  | DS
14 | 462000 |  |  |  | 50 |  | 24 |  |  | 1.0392 |  |  | 1 |  |  | SN
15 | 681000 | [5 empty] | 37 |  |  | 1.0823 |  |  | 1.1 |  |  | TM
16 | 2565000 |  |  |  | 50 |  | 155 |  |  | 1.1926 |  |  | 1.2 |  |  | SN
17 | 1554000 | [5 empty] | 90 |  |  | 1.1471 |  |  | 1 |  |  | DS
18 | 1805000 |  |  |  | 50 |  | 87 |  |  | 0.97145 |  |  | 0.9 |  |  | DS
19 | 909000 |  |  |  | 50 |  | 58 |  |  | 1.2536 |  |  | 1.3 |  |  | SN
20 | 667000 | [5 empty] | 50 |  |  | 1.4553 |  |  | 1.2 |  |  | TM
21 | 857000 | [5 empty] | 56 |  |  | 1.2814 |  |  | 1.1 |  |  | SN
22 | 750000 |  |  |  | 50 |  | 45 |  |  | 1.1848 |  |  | 1 |  |  | DS
23 | 2219000 | [5 empty] | 145 |  |  | 1.2814 |  |  | 1.3 |  |  | DS
24 | 1977000 |  |  |  | 50 |  | 140 |  |  | 1.3803 |  |  | 1.3 |  |  | DS
25 | [15 empty] | DS - Plant Offline
26 | 2921000 |  |  |  | 50 |  | 198 |  |  | 1.3256 |  |  | 1.2 |  |  | DS
27 | 3039000 |  |  |  | 50 |  | 227 |  |  | 1.4505 |  |  | 1.3 |  |  | DS
28 | 3054000 |  |  |  | 50 |  | 215 |  |  | 1.3728 |  |  | 1.4 |  |  | DS
29 | 2622000 |  |  |  | 50 |  | 0 |  |  | 0.1 |  |  | 0.9 |  |  | DS - Chemical pump was air bound
30 | 910000 |  |  |  | 50 |  | 55 |  |  | 1.1927 |  |  | 1.2 |  |  | SN
31 | 1980000 | [5 empty] | 129 |  |  | 1.2779 |  |  | 1.2 |  |  | SN
Totals | 44958000 |  |  |  | 750 |  | 2715 | [8 empty] | If you use a saturator: calculate monthly
Average | 1498600 |  |  |  | 25 |  | 90.5 |  |  | 1.1988 |  |  | 1.1333 |  |  | Fluoride Ion Dosage |  |  |  | 0.99583 | ppm
Notes: 1) If you use a saturator you must calculate a monthly fluoride ion dosage based on pounds used.
2) If you use a Mass. certified lab. for daily sampling, attach a copy of your Mass. approved lab analytical report form to this report.
3) All pumping fluoridated sources MUST be tested daily for fluoride at the entry point to the distribution system or near the point of fluoride application.
4) The optimum fluoride level is 0.7 mg/L. | [13 empty] | 5) Report all Fluoride results to the nearest tenth.
6) For Fluoride issues that require reporting, notify DPH at 617-624-5573 AND MassDEP Drinking Water Program Regional Office or 617-292-5770.
I certify under penalty of law that I am the person authorized to fill out this form and the information contained herein is true, accurate and
complete to the best of my knowledge and belief.
Name of PWS certified operator or responsible party: | [12 empty] | Signature: | [5 empty] | Date:
Phone #: | (978) 999-9999 |  |  |  |  | Fax#: | (978) 999-9998 | [6 empty] | Email address: | xxx@xxxx.com
Section IV: DPH USE: | [5 empty] | Date received: | [5 empty] | Comments:
PWSs approved by MassDEP for Fluoridation treatment must return all applicable pages (A, B &C) of this report form by the 10th day following the
reporting month to: MassDPH, 250 Washington Street-5th floor, Boston, MA 02108. Attention: Office of Oral Health DPH Fluoride Form A -5-24-07
Prepared by H2O Software, (978) 877-0352, lguilmartin@cs.com
Cu Ft
Gals or