| Location/ Room | Occupants in Room | Temp (°F) | Relative Humidity (%) | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | PM2.5 (µg/m3) | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| background |  | 81 | 28 | 391 | ND | 12 |  |  |  |  |
| 326 | 0 | 76 | 31 | 480 | ND | 6 | Y | Y |  | Plants on univent, FC, TB, cleaner, clutter |
| 327 | 0 | 76 | 31 | 482 | ND | 7 | Y |  | Y | FC, Food, microwave, 2 computers., windows open, dust on vent |
| 328 | 0 | 76 | 29 | 495 | ND | 7 | Y | N | N | DO, WDCT |
| 330 | 0 | 76 | 28 | 446 | ND | 7 | Y | N |  | DO, damaged floor tile (9x9”), possible asbestos, WDCT near light fixture, penetrations of pipes through floors |
| 329 | 0 | 76 | 28 | 526 | ND | 7 | N | N | N | DO |
| 340 | 0 | 78 | 30 | 729 | ND | 7 | Y | N | N | DO |
| Gym | 0 | 77 | 29 | 446 | ND | 7 | N | Y univents above both doors | Y below stage |  |
| Photocopy Room | 0 | 76 | 24 | 419 | ND | 7 | Y | N | Y small fan mounted on wall | DO Laminator near entry door Strong plastic odor near entry door Floor tiles in disrepair Water damaged ceiling plaster Efflorescence on ceiling 2 wet toner copiers |
| 1st floor 3-7 | 15 | 77 | 34 | 964 | ND | 10 | Y | Y univent |  | missing CT, univent covered with papers, rusty water in sink |
| 3-6 | 14 | 77 | 31 | 578 | ND | 9 | Y | Y | Y In closet | DO, univent blocked by books, TB, Occupant reported and it was confirmed that rusty water was coming out of faucet of sink in classroom. |
| Girls Rest Room |  |  |  |  |  |  | Y | N | Y Exhaust is in wall behind toilets | DO, bucket located under one sink due to possible leak. |
| 112 | 7 | 78 | 32 | 544 | ND | N/A* | Y | Y |  | windows open, univent covered with documents, teacher states paper placed on bulletin board exhibited mold. (Paper had been discarded and new paper was covering the bulletin board) |
| 113 | 0 | 78 | 29 | 432 | ND | N/A* | Y | Y |  | windows open, PF, CD, univent covered, Windex in classroom |
| 114 | 21 | 79 | 31 | 675 | ND | N/A* | Y | Y |  | DO, PF(2) |
| 115 | 0 | 78 | 29 | 432 | ND | 8 | Y | Y |  | DO, WDCT, WD carpet, windows open |
| 116 Library | 0 | 78 | 29 | 485 | ND | 7 | Y | Y | Y | water damage and mold colonization on ceiling of bowed window, ducts exhibit breaches, occupants state they experience a chronic ant problem and that there is a bird’s nest near the ceiling. |
| 138 Art Room | 18 | 78 | 30 | 628 | ND | N/A* | Y | Y |  | WDCTs, many papers in room, windows open, spray disinfectant, Comet cleanser observed. |
| 473 Cafeteria | 0 | 80 | 30 | 447 | ND | 8 | Y | Y | Y | Discolored wall |
| 236 | 22 | 79 | 29 | 686 | ND | 9 | Y | Y |  | DO, Windows open, PF, AD, 2 computers, Broken CTs, Ajax cleanser Unit Ventilator Exhaust off |
| 232 | 15 | 79 | 30 | 648 | ND | 9 | Y | Y |  | DO, Numerous WDCTs, Windows open, Lysol spray cleaner Unit Ventilator Exhaust off |
| 215 | 0 | 79 | 32 | 646 | ND | 6 | Y | Y |  | DO, Missing CT, univent covered |
| 242 | 0 | 78 | 28 | 444 | ND | 7 | Y | Y |  | DO, PF, WDCT, Missing CT PF Unit Ventilator Exhaust off |
| 246 | 23 | 79 | 35 | 1796 | ND | 9 | Y | Y |  | TB, DEM, PF, Windows open, excessive paper on all surfaces Unit Ventilator Exhaust off |
| 247 | 6 | 79 | 31 | 961 | ND | 12 | Y | Y |  | DO, WDCT, Window open, univent covered Unit Ventilator Exhaust off |
| 248 | 1 | 79 | 30 | 600 | ND | 8 | Y | Y |  | TB, PF, FC, AD, 2 Comp., Window open, Cylinder of compressed oxygen on window sill – appeared to belong to an individual for health reasons. |
| Women’s Room |  |  |  |  |  |  |  |  | Y Covered with dust | Water damaged ceiling with efflorescence |
| 258 | 2 | 80 | 27 | 494 | ND | 7 | Y | Y | y | DO, Window open, WDCTs, 1 comp., unlabeled spray bottle Unit Ventilator Exhaust off |
| 257 | 0 | 80 | 26 | 470 | ND | 7 | Y | Y | y | Plants over univent, windows open, WDCT Unit Ventilator Exhaust off |
| 256 | 0 | 80 | 27 | 601 | ND | 9 | Y | Y | y | WDCT, DO, PF, CD, 2 comp. Unit Ventilator Exhaust off |
| 255 | 0 | 80 | 28 | 690 | ND | 9 | Y | Y | y | DO, missing CT, TB, PF, Multiple WDCTs, AD, Spray cleanser, Chlorox Greenworks Unit Ventilator Exhaust off |
| 26 | 16 | 80 | 28 | 551 | ND | 7 | Y | Y | y | DO, Ceiling Fan, PF, windows open Unit Ventilator Exhaust off |
| 2-8 | 14 | 80 | 27 | 491 | ND | 8 | Y | Y |  | PF, Buckled WDCT, possible asbestos on pipe |
| 4 Nurses’ Room | 2 | 78 | 33 | 664 | ND | 19 | Y | Y | Y | DO, Exhaust from restroom may go into back closet of nurses room. Sump in back room |
| 2 | 1 | 77 | 35 | 723 | ND | 9 | Y | N | N | DO, AP, Efflorescence on wall/window area, PF, frayed carpet |
| 025 | 0 | 79 | 33 | 602 | ND | 7 | Y | Y | N | DEM, univent blocked |
| 511 | 0 | 80 | 30 | 572 | ND | 8 | Y | Y | N | DO, window open |
| 024 | 0 | 81 | 29 | 622 | ND | 8 | Y | Y | N | DO |
| 003 | 16 | 80 | 31 | 833 | ND | 9 | Y | Y | N | PF, DEM |
| 342 | 20 | 78 | 33 | 659 | ND | 10 | Y | Y | Y | Ceiling fan Window open cleaners |
| 343 | 22 | 79 | 30 | 545 | ND | 9 | Y | Y | Y | Window open Tennis balls on chairs Bird’s nest in univent Sink running water continuously |
| 344 | 0 | 79 | 27 | 407 | ND | 5 | Y | Y | Y | Ceiling fan |
| 345 | 25 | 79 | 29 | 575 | ND | 9 | Y | Y | Y | Ceiling fan Tennis balls on chairs |
| 346 | 0 | 79 | 28 | 482 | ND | 6 | Y | Y | Y | Exhaust vent obstructed by curtain cleaners |
| 315 | 18 | 78 | 35 | 648 | ND | 8 | Y | Y | Y | PF Water damaged ceiling |
| 314 | 18 | 79 | 33 | 508 | ND | N/A* | Y | Y | Y | PF |
| 313 | 19 | 79 | 33 | 722 | ND | N/A* | Y | Y | Y | DEM 4 AT |
| 312 | 17 | 79 | 33 | 732 | ND | N/A* | Y | Y | Y |  |
| 311 | 13 | 79 | 33 | 526 | ND | N/A* | Y | Y | Y | AT |
| 108 | 0 | 77 | 34 | 561 | ND | 7 | Y | Y | Y |  |
| 105 | 1 | 78 | 33 | 661 | ND | 17 | Y | Y | Y | Reported water damaged carpet |
| 107 | 0 | 79 | 34 | 581 | ND | 12 | y | y | y | Clutter |
| 106 | 1 | 78 | 30 | 518 | ND | 6 | Y | Y | Y | Soap odor |
| Gymnasium south building | 15 | 79 | 31 | 580 | ND | N/A* | Y | Y | Y | Damage to ceiling |
| 223 | 0 | 76 | 35 | 599 | ND | N/A* | Y | N | N |  |
| 215 | 0 | 77 | 35 | 425 | ND | 6 | Y | Y | Y | Supply off Unit ventilator exhaust off |
| 243 | 22 | 78 | 37 | 818 | ND | N/A* | Y | Y | Y | Supply off Unit ventilator exhaust off |
| 252 | 0 | 81 | 32 | 712 | ND | N/A* | Y | Y | Y | Supply off Unit ventilator exhaust off |
| 244 | 0 | 78 | 33 | 448 | ND | N/A* | Y | Y | Y | Supply off Unit ventilator exhaust off |
| 253 | 0 | 80 | 30 | 504 | ND | N/A* | Y | Y | Y | Supply off Unit ventilator exhaust off |
| 012 | 0 | 79 | 34 | 678 | ND | 9 | Y | Y | N | Supply off Supply blocked Clutter |
| 010 | 0 | 81 | 33 | 701 | ND | N/A* | Y | Y | N | Supply off |
| 009 | 0 | 80 | 29 | 489 | ND | 9 | Y | Y | N | Clutter Pets Pet bedding on carpet |
| 29-30 | 14 | 79 | 35 | 843 | ND | N/A* | Y | Y | N | Supply off |
| 29-31 | 0 | 79 | 32 | 451 | ND | 8 | Y | Y | N |  |