## Slide 1: MA LONG DURATION STORAGE STUDY ****** FEEDBACK FROM: Dr. Richard (Dick) Giberti dickgiberti@gmail.com
        What stakeholder applications should be included in the study?
        Suggestions
        Residential / Commercial
        Community
        Microgrids
        Virtual Power Plants
        Utilities / Independent Power Producers (IPP’s)
        Current Applications
        Peak Shaving / Energy Transfer
        Arbitrage
        Future Applications
          Load following
Different technologies are better suited to the needs of different renewable energy storage applications

## Slide 2: MA LONG DURATION STORAGE STUDY ********** FEEDBACK FROM Dr. Richard (Dick) Giberti dickgiberti@gmail.com
What Kind ? / How Much (Duration)?
  Peak Shaving / Energy Transfer / Arbitrage
      “How much” is an economic based decision by the stakeholder
      Typically 2 -4 hours duration in projects over the past few years
      Seeing longer durations as ITC’s have been extended in the 2022 IRA

## Slide 3: MA LONG DURATION STORAGE STUDY ********** FEEDBACK FROM Dr. Richard (Dick) Giberti dickgiberti@gmail.com
Load Following
Needed to replace fossil fired load following plants as they are shut down
How much load following capacity will be shut down in Massachusetts?
Is 2 – 4 hours duration storage currently being installed adequate for load following?
Conclusions from a personally developed load following model:
    2 – 4 times as much solar capacity as the maximum daily load could be needed as a typical daily load is being followed on bright sunny days depending on the extent of the renewables employed
    (100 MW Max. Load – 200 MW to 400 MW Solar)
    Storage capacity of 3 – 14 hours times the maximum daily load could be needed as for a typical daily load being followed on a bright sunny days depending on the % of the renewables employed
    (100 MW Max. Load – 300 MWh to 1,400 MWh storage)
    To compensate for a cloudy day every other day, a storage capacity 8 hours times the storage capacity as would be needed for a series of three sunny days could be needed even at only 25% renewables.
    (300 MWh’s for consecutive sunny days – 2,400 MWh’s for 1 cloudy day every other day)
    This will significantly increase as the % of renewals increases
The future amount of storage is being grossly underestimated by the electrical power industry

## Slide 4: MA LONG DURATION STORAGE STUDY ********** FEEDBACK FROM Dr. Richard (Dick) Giberti dickgiberti@gmail.com
Identify Storage Characteristics to be studied and reported on in the study
Suggestions:
Status of demonstration or development
  Date or expected date of commercialization
Bankability (Likelihood of securing funding)
Capital and Operating Cost (including disposal / recycle costs)
Round trip storage efficiency
Inherent Technology Risks
Safety / Environmental Risks
Pros and Cons for each stakeholder application
Vendors

## Slide 5: MA LONG DURATION STORAGE STUDY ********** FEEDBACK FROM Dr. Richard (Dick) Giberti dickgiberti@gmail.com
Suggested Storage Technologies for Inclusion in the Study
  Lithium-ion batteries
  Sodium-ion batteries (Natron)
  Redox flow batteries
  Vanadium (Infinity)
  Iron (ESS)
  Gravity – Lifting / Lowering Solids (Energy Vault)
  Compressed CO2 (Energy Dome)
  Iron-Air batteries (Form Energy)
  Zinc batteries (EOS)
  Hydrogen
  Other Battery Technologies Likely to be Commercialized
  and Economically Competitive in the Next 5-10 Years
  Solid-State Lithium-ion
  Hydro Pneumatic Energy Storage (for offshore wind turbines)