The Commonwealth of Massachusetts

Executive Office of Health and Human Services

Department of Public Health

250 Washington Street, Boston, MA 02108-4619

Sterile Compounding Compliance Checklist

If the proposed design meets the listed requirement, please indicate by placing “Y” (yes) or “N” (no) and include comments as to the reason for the non-compliance and plans to mitigate.  If not applicable, indicate with “NA”.

Please note that this is not an all-inclusive list of proposed standards in Draft 247 CMR 17.00 or the requirements of USP.  At a minimum, applicants are required to adhere to the standards set forth in the most recent version of USP <797> and USP <800>. It is the responsibility of the applicant to be familiar with the requirements set forth in USP chapters and the Board’s regulations.

| Draft 247 CMR 17.00 | Citation | Y/N | Comments |
| --- | --- | --- | --- |
| Miscellaneous |  |  |  |
| A pharmacy may not compound non-sterile preparations in any Primary Engineering Control (PEC) or Secondary Engineering Control (SEC) used for sterile compounding. | 17.03(8) |  |  |
| A pharmacy shall have a dedicated changing area for sterile compounding personnel. | 17.04(2) |  |  |
| Primary Engineering Controls (PECs) |  |  |  |
| A pharmacy shall utilize only commercially manufactured PECs. | 17.06(1) |  |  |
| All Secondary Engineering Controls (SECs) |  |  |  |
| The doors leading into and between ISO Classified SECs shall be constructed with an interlocking design or utilize an alternative method to ensure that doors are not opened simultaneously. | 17.07(1)(c) |  |  |
| Unless prohibited by local building or fire code, an SEC may not have more than one door to immediately adjacent areas. | 17.07(1)(b) |  |  |
| Each newly constructed SEC shall allow for visual observation through windows or technology. | 17.07(1)(a) |  |  |
| SECs may not contain windows to the outdoors. | 17.07(1)(k) |  |  |
| A pharmacy shall ensure that any pass-through chambers: - have an interlocking door design; and - are not refrigerator units. | 17.04(1) |  |  |
| Walls shall be made of solid surface materials such as locking sealed panels or epoxy-coated gypsum board. | 17.07(1)(j) |  |  |
| Ceiling panels, fixtures, and other penetrations through the ceiling or walls shall be smooth and sealed around the perimeter. | 17.07(1)(h) |  |  |
| SECs shall utilize light fixtures designed for sterile compounding areas (i.e., cleanroom grade) that have an exterior surface that is smooth, mounted flush with the ceiling, and sealed. | 17.07(1)(g) |  |  |
| Sprinkler heads shall be recessed, covered, and easily cleanable. | 17.07(1)(i) |  |  |
| Floors shall be composed of wide sheet vinyl that is heat sealed at the seams, or other solid, smooth surface, and coved at the wall or appropriately sealed. | 17.07(1)(l) |  |  |
| SECs may not contain floor drains. | 17.07(1)(f) |  |  |
| A pharmacy may not locate a refrigerator in any ISO Classified SEC. | 17.07(1)(e) |  |  |
| A pharmacy may not use ISO Classified areas for drug storage. | 17.04(3) |  |  |
| Ante Rooms |  |  |  |
| A newly constructed ante room shall be at least 72 square feet. | 17.07(3)(a) |  |  |
| For hand hygiene, an anteroom shall have a stainless-steel sink that is located on the clean side of the line of demarcation at least one meter away from the buffer room door. | 17.07(3)(b) |  |  |
| # The stainless-steel sink shall: - be equipped with hands-free controls for water and soap dispensing; - have proper depth and capacity for hand washing up to the elbows; - minimize splashing and dripping of water; - be designed to prevent standing water; and - have a faucet that does not have an aerator mechanism on the nozzle. | 17.07(3)(c) |  |  |
| # An ante room shall have low-lint, disposable towels located in close proximity to the sink. | 17.07(3)(d) |  |  |
| Buffer Rooms |  |  |  |
| A newly constructed non-hazardous drug buffer room shall be at least 100 square feet. | 17.07(2)(a) |  |  |
| # A newly constructed hazardous drug buffer room shall be at least 72 square feet. | 17.07(2)(b) |  |  |
| Buffer room doors shall be hands-free. | 17.07(2)(c) |  |  |
| HVAC |  |  |  |
| Newly constructed ISO Classified SECs shall utilize a closed loop ducted system, a sealed plenum system, or equivalent HVAC design. | 17.05(1) |  |  |
| Supply air provided for each ISO Classified SEC shall be provided exclusively through ceiling mounted HEPA filters. | 17.05(3) |  |  |
| Air returns in ISO Classified SECs shall be mounted low on the walls | 17.05(4) |  |  |
| If utilized, relief air vents shall be mounted low on the wall and designed to prevent the ingress of less clean air or contaminants from adjacent areas. | 17.05(5) |  |  |
| Temperature/Humidity |  |  |  |
| A pharmacy shall have a system to continuously measure the temperature and humidity of each SEC. The quantitative results shall be reviewed and documented at least daily on all days the pharmacy is open. | 17.10(3) |  |  |
| SECs shall maintain a temperature of 68 degrees Fahrenheit (20 degrees Celsius) or lower. | 17.10(1) |  |  |
| SECs shall maintain relative humidity of 60% or lower. | 17.10(2) |  |  |

Please direct any questions to:	Pharmacy.Admin@mass.gov