The Commonwealth of Massachusetts

Executive Office of Health and Human Services

Department of Public Health

Bureau of Environmental Health

Community Sanitation Program

5 Randolph Street

Canton, MA 02021

Telephone: (781)828-7910

Facsimile: (781)828-7703

DEVAL L. PATRICK GOVERNOR TIMOTHY P. MURRAY LIEUTENANT GOVERNOR JUDYANN BIGBY, MD SECRETARY JOHN AUERBACH COMMISSIONER

March 25, 2010

Andrea J. Cabral, Sheriff

Suffolk County Jail

200 Nashua Street

Boston, MA 02214

Re: Facility Inspection

Dear Sheriff Cabral:

In accordance with M.G.L. c. 111, §§ 5, 20, and 21, and Department of Public Health Regulations 105 CMR 451.000: Minimum Health and Sanitation Standards and Inspection Procedures for Correctional Facilities; 105 CMR 480.000: Storage and Disposal of Infectious or Physically Dangerous Medical or Biological Waste (State Sanitary Code, Chapter VIII); 105 CMR 590.000: Minimum Sanitation Standards for Food Establishments (State Sanitary Code Chapter X); the 1999 Food Code; and 105 CMR 205.000 Minimum Standards Governing Medical Records and the Conduct of Physical Examinations in Correctional Facilities; I conducted an inspection of Suffolk County Jail on March 22, 2010 accompanied by Angel Lopez, Fire Safety and Environmental Health Safety Officer. Violations noted are listed below (* indicates conditions documented on previous inspection reports).

Entry Level

Front Lobby

No Violations Noted

Men’s Room

No Violations Noted

Women’s Room

105 CMR 451.126	Hot Water: Hot water temperature recorded at 900F

7th Floor

Visiting Room Hallway

105 CMR 451.350	Structural Maintenance: Wall damaged near visiting room # 701 and 712

Floor 6.5

Gym

105 CMR 451.344	Illumination in Habitable Areas: Several light fixtures not working properly

105 CMR 451.353	Interior Maintenance: Wall and floor dirty near water fountain

Staff Bathroom #6503

No Violations Noted

Storage Room # 6504

105 CMR 451.123	Maintenance: Ceiling repair unfinished

Inmate Bathroom # 6505

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No soap at handwash sink

105 CMR 451.123	Maintenance: Floor dirty

105 CMR 451.126	Hot Water: Hot water temperature recorded at 660F

Inmate Bathroom # 6506

105 CMR 451.110(A)*	Hygiene Supplies at Toilet and Handwash Sink: No paper towels at handwash sink

105 CMR 451.110(A)*	Hygiene Supplies at Toilet and Handwash Sink: No soap at handwash sink

105 CMR 451.126	Hot Water: Hot water temperature recorded at 660F

6th Floor

Staff Bathroom 6-1 & 6-2

No Violations Noted

Staff Bathroom 6-3 & 6-4

No Violations Noted

Unit 6-1A

Common Area

No Violations Noted

Kitchenette

FC 6-301.11*	Numbers and Capacity; Handwashing Facilities: No soap at handwash sink

FC 6-301.12	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket and 	no sanitizer solution available

FC 4-601.11(c)*	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty, hot 	holding tray dirty

Shower Area

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty and rusted

105 CMR 451.123*	Maintenance: Light fixture rusted

105 CMR 451.123	Maintenance: Wall tiles missing near door frame

Cells

No Violations Noted

Unit 6-1

Common Area

105 CMR 451.350	Structural Maintenance: Wall damaged outside cell # 29 and 30

105 CMR 451.353	Interior Maintenance: Food debris and dirty observed on window sills

105 CMR 451.353	Interior Maintenance: Water fountain dirty

Kitchenette

FC 6-301.12	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

Shower # 617

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Floor tiles missing near drain cover

105 CMR 451.123	Maintenance: Ceiling damaged

Shower # 618

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Possible mold growth on shower tiles

Shower # 711

105 CMR 451.123*	Maintenance: Shower walls need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Walls and floor dirty

Shower # 712

105 CMR 451.123*	Maintenance: Shower walls need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Walls and floor dirty

105 CMR 451.123	Maintenance: Possible mold growth on shower tiles

Cells

105 CMR 451.353	Interior Maintenance: Ceiling dirty in cell # 39

Unit 6-2

Common Area

105 CMR 451.353	Interior Maintenance: Chair damaged in TV area

Kitchenette

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket and 	no sanitizer solution available

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated hard 	boiled eggs observed in kitchenette

Slop Sink Room # 62B

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, water control handle leaking

Shower # 625

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

Shower # 626

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

Meeting Room # 627

No Violations Noted

Shower # 721

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Shower head missing

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower out of order

Shower # 722

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Ceiling vent dirty

Shower # 723

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123*	Maintenance: Possible mold growth on ceiling

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 4, 5, 11, and 12

105 CMR 451.103	Mattresses: Mattress damage in cell # 3

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 7, 15, and 20

Unit 6-3

Common Area

105 CMR 451.353*	Interior Maintenance: Food debris and dirty observed on window sills

Kitchenette

FC 4-602.12(B)	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

Shower # 63C

105 CMR 451.123*	Maintenance: Shower walls need re-grouting

105 CMR 451.123*	Maintenance: Step tiles missing

105 CMR 451.123	Maintenance: Wall tiles damaged near door frame

Slop Sink Room # 63D

105 CMR 451.353	Interior Maintenance: Vent dirty

Shower # 63E

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Floor tiles dirty

Shower # 63G	Shower Occupied at the Time of Inspection

Shower # 63H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Ceiling vent dirty

Shower # 63J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Door frame rusted

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 2

Unit 6-4

Common Area

105 CMR 451.353	Interior Maintenance: Food debris and dirty observed on window sills

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged near cell # 39 and 40

Kitchenette

No Violation Noted

Shower # 64B

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Ceiling dirty

Slop Sink Room # 64C

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

105 CMR 451.353	Interior Maintenance: Wall dirty

Shower # 64D

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Vent rusted

105 CMR 451.123	Maintenance: Ceiling paint damaged

Shower # 64E

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Floor tiles missing near drain cover

105 CMR 451.123*	Maintenance: Shower tiles dirty

105 CMR 451.123*	Maintenance: Door frame rusted

105 CMR 451.123*	Maintenance: Ceiling vent dirty and rusted

Shower # 64G

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Shower tiles dirty

105 CMR 451.123*	Maintenance: Door frame rusted

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Ceiling paint damaged

Shower # 64H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Upper edge of tiles not sealed properly to ceiling

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 1 and 14

105 CMR 451.353	Interior Maintenance: Ceiling dirty in cell # 11

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 37

5TH Floor

Visiting Room Hallway

No Violations Noted

Medical Area

Waiting Room

No Violations Noted

Nursing Area

105 CMR 451.353	Interior Maintenance: Counter top front at handwash sink damage and no longer 	easily cleanable

Omni Cell Room # 5041

No Violations Noted

Diabetic Room # 5044

No Violations Noted

Male Staff Locker and Bathroom # 5093

105 CMR 451.353	Interior Maintenance: Wall damaged

Female Staff Locker and Bathroom # 5124

No Violations Noted

Staff Break Room # 5033

FC 4-204.112(A)*	Design and Construction, Functionality: No functioning thermometer in refrigerator

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, shelf missing from refrigerator unit

FC 4-601.11(A)*	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, interior 	surfaces of refrigerator unit dirty and disorganized

FC 4-602.12(B)*	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

Dental Office

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet leaking

Exam Room # 1 and Bathroom # 5032

105 CMR 451.353	Interior Maintenance: Backsplash loose

Exam Room # 2 and Bathroom # 5030

Occupied at the time of inspection

X-Ray Room

No Violations Noted

Medical Waste Storage Room # 5507

No Violations Noted

Medical Housing Unit

Common Area

105 CMR 451.353	Interior Maintenance: Vent dirty

Kitchenette

FC 6-301.12	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

Isolation Cell # 5514

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No soap at handwash sink

105 CMR 451.110(B)	Hygiene Supplies at Toilet and Handwash Sink: No waste receptacle at handwash sink

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, handwash sink not working 	properly

Shower # 5512

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty and rusted

105 CMR 451.123*	Maintenance: Shower wall and floor dirty

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, vent painted over

Shower # 5554

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Shower wall dirty

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, vent painted over

Cells

105 CMR 451.353	Interior Maintenance: Vent dirty in cell # 5517

105 CMR 451.353	Interior Maintenance: Wall dirty in cell # 5563

Psychiatric Housing Unit # 5552

Kitchenette

FC 6-301.12*	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

Shower # 5573

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Paint on light fixture damaged

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, vent painted over

Slop Sink Room

105 CMR 451.353	Interior Maintenance: Wet mop not hung properly

Cells

No Violations Noted

4th Floor

Staff Bathroom 4-1 & 4-2

105 CMR 451.123	Maintenance: Ceiling vent dirty

Staff Bathroom 4-3 & 4-4

105 CMR 451.353	Interior Maintenance: Door # 343 dirty outside staff bathroom

Unit 4-1

Common Area

105 CMR 451.350	Structural Maintenance: Floor tile missing outside shower # 41K

Kitchenette

FC 6-301.12	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket and 	no sanitizer solution available

Slop Sink Room # 41N

105 CMR 451.353	Interior Maintenance: Floor dirty

Room # 41M

105 CMR 451.353	Interior Maintenance: Floor dirty

105 CMR 451.353	Interior Maintenance: Missing wire covers

Shower # 41G

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Step and wall tiles damaged

105 CMR 451.123	Maintenance: Interior access door paint damaged

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Wall tiles dirty

Shower # 41H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Light fixture and vent rusted

105 CMR 451.123	Maintenance: Step tiles damaged

105 CMR 451.123	Maintenance: Wall tiles dirty

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, shower head leaking

Shower # 41I

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Interior access door paint damaged

Shower # 41J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

Shower # 41K

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Vent rusted

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Floor tiles missing near drain

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 20, 22, 30, 32, and 33

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 17 and 18

Unit 4-2

Common Area

105 CMR 451.350	Structural Maintenance: Floor tiles damaged near stairway

105 CMR 451.353	Interior Maintenance: Vent dirty outside shower unit

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Light fixture not working properly 	outside cell # 18

Kitchenette

FC 2-402.11	Hygienic Practices; Hair Restraints: Food service personnel not wearing appropriate 	hair restraints, no beard guards provided

FC 6-301.11	Numbers and Capacity; Handwashing Facilities: No soap at handwash sink

FC 6-301.12	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

Slop Sink Room # 42C

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

Shower # 42D

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Ceiling paint damaged

Shower # 42E

105 CMR 451.123*	Maintenance: Shower walls need re-grouting

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Ceiling damaged in corner

Room # 42F

105 CMR 451.353	Interior Maintenance: Wall vent dirty

Shower # 42G

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Door frame rusted

105 CMR 451.123	Maintenance: Ceiling dirty

105 CMR 451.123	Maintenance: Shower curtain damaged

Shower # 42H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123*	Maintenance: Metal access door rusted

Shower # 42J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Door frame rusted

105 CMR 451.123	Maintenance: Floor tiles missing near wall

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Step tiles loose

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head leaking

Cells

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 30, 31, 32, and 34

Unit 4-3

Common Area

105 CMR 451.353	Interior Maintenance: Vent dirty outside slop sink room # 43D

105 CMR 451.353	Interior Maintenance: Window sills dirty near cell # 12 and 29

Kitchenette

FC 2-401.11	Hygienic Practices Food Contamination Prevention: Food service personnel eating in 	an inappropriate area

FC 2-402.11	Hygienic Practices; Hair Restraints: Food service personnel not wearing appropriate 	hair restraints, no beard guards or hair nets provided

FC 3-304.15(A)	Preventing Contamination from Utensils: Ungloved hand used to hand out food try

FC 4-602.12(B)	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

FC 6-301.11	Numbers and Capacity; Handwashing Facilities: No soap at handwash sink

FC 6-301.12	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

Shower # 43C

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Soap scum on walls in shower

105 CMR 451.123	Maintenance: Metal ceiling plate and light fixture rusted

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head leaking

Slop Sink Room # 43D

105 CMR 451.353	Interior Maintenance: Vent dirty

Shower # 43E

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Ceiling vent dirty

Shower # 43G

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Metal access plate on ceiling rusted

105 CMR 451.123*	Maintenance: Floor tiles missing

105 CMR 451.123	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Possible mold growth on ceiling

Shower # 43H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Floor tiles missing

105 CMR 451.123*	Maintenance: Possible mold growth on ceiling

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Wall tiles damaged

105 CMR 451.123	Maintenance: Soap scum and mold growth on wall tiles

Shower # 43I

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Possible mold growth on ceiling

105 CMR 451.123*	Maintenance: Door frame rusted

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Wall tiles damaged

105 CMR 451.123	Maintenance: Floor tiles missing near drain

Cells

105 CMR 451.353	Interior Maintenance: Ceiling dirty in cell # 32

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 5, 8, 9, 14, 28, 30, 31, and 33

Unit 4-4

Common Area

105 CMR 451.353	Interior Maintenance: Window sills dirty near cell # 5 and 24

105 CMR 451.353	Interior Maintenance: Wall dirty near cell # 5

Kitchenette

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket and 	no sanitizer solution available

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty, water 	fountain dirty

FC 6-301.11	Numbers and Capacity; Handwashing Facilities: No soap at handwash sink

FC 6-301.12	Numbers and Capacity; Handwashing Facilities: No hand drying method available at 	handwashing sink

Shower # 44B

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Metal access plate on ceiling rusted

105 CMR 451.123	Maintenance: Soap scum on wall tiles in shower

105 CMR 451.123	Maintenance: Ceiling damaged near ceiling vent

105 CMR 451.123	Maintenance: Wall tiles damaged

Slop Sink Room # 44C

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

Shower # 44D

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Light fixture rusted

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Wall tiles damaged

Meeting Room # 44E

No Violations Noted

Shower # 44F

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

Closet # 44G

105 CMR 451.353	Interior Maintenance: Ceiling fire-retardant insulation not intact

Shower # 44H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Shower curtain missing

105 CMR 451.123*	Maintenance: Vent rusted

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Possible mold growth on ceiling

Shower # 44I

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Step tiles missing

105 CMR 451.123	Maintenance: Door frame rusted

Shower # 44J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Ceiling paint damaged

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 7

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 3, 8, 12, 14, 27, and 28

Floor 3.5

Office Area

No Violations Noted

Slop Sink Room # 3503

105 CMR 451.353	Interior Maintenance: No light shield in maintenance area

Female Staff Bathroom

105 CMR 451.123	Maintenance: Wall and vent dirty above toilet stalls

Male Staff Bathroom

No Violations Noted

File Room Kitchenette

No Violations Noted

2nd Floor

Staff Bathroom 2-1 & 2-2

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, hot water handle leaking

Staff Bathroom 2-3 & 2-4

105 CMR 451.123	Maintenance: Ceiling vent dirty

Unit 2-1

Common Area

No Violations Noted

Kitchenette

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket and 	no sanitizer solution available

FC 6-101.11(A)(1)	Materials for Construction and Repairs: Surface not easily cleanable, counter top 	under microwave oven damaged

Shower # 21B

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty and rusted

105 CMR 451.123*	Maintenance: Step tiles damaged

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Possible mold growth on ceiling

Slop Sink Room # 21C

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

Shower # 21D

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Wall tiles damaged

105 CMR 451.123*	Maintenance: Light fixture damaged

105 CMR 451.123	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Handicap shower head hose damaged

105 CMR 451.123	Maintenance: Ceiling vent dirty

Meeting Room # 21E

No Violations Noted

Shower # 21F

105 CMR 451.123	Maintenance: Shower walls need re-grouting

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Flying insects observed in shower area

Shower # 21G

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Possible mold growth on ceiling

105 CMR 451.123*	Maintenance: Shower head loose

105 CMR 451.123	Maintenance: Wall tiles damaged

105 CMR 451.123	Maintenance: Door rusted

105 CMR 451.123	Maintenance: Ceiling paint damaged

Closet # 21H

No Violations Noted

Shower # 21J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Wall tiles missing near door frame

105 CMR 451.123	Maintenance: Ceiling paint damaged

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 3

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 5, 15, 17, 18, and 28

Unit 2-2

Common Area

105 CMR 451.353	Interior Maintenance: Window sills dirty near cell # 6

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty outside slop sink room # 22D and shower # 	22H

Kitchenette

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket and 	no sanitizer solution available

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty, water 	fountain dirty

FC 4-602.12(B)	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not properly cleaned, handwash sink 	dirty

Meeting Room # 22B

No Violations Noted

Shower # 22C

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Wall tiles dirty

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Possible mold growth on ceiling

Slop Sink Room # 22D

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

Shower # 22E

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling damaged in corner

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123*	Maintenance: Wall tiles dirty

105 CMR 451.123	Maintenance: Shower curtain missing

Shower # 22J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Ceiling damaged in corner

105 CMR 451.123*	Maintenance: Door frame rusted

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Step tiles damaged

Shower # 22I

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Wall tiles dirty

105 CMR 451.123	Maintenance: Floor drain cover missing

105 CMR 451.123	Maintenance: Vent cover rusted

105 CMR 451.123	Maintenance: Possible mold growth on ceiling

Shower # 22H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Access panel on ceiling rusted

105 CMR 451.123*	Maintenance: Floor tiles missing near drain

105 CMR 451.123	Maintenance: Ceiling vent dirty and rusted

Cells

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, hot water controls not working 	properly in cell # 9

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 5, 10, 11, 13, 14, 15, 17, 20, 25, 26, 28, 30, 33, and 34

Unit 2-3

Common Area

105 CMR 451.353	Interior Maintenance: Window sills dirty near cell # 12

105 CMR 451.353	Interior Maintenance: Vent dirty outside shower # 23C and 23G

Kitchenette

No Violations Noted

Meeting Room # 23B

No Violations Noted

Shower # 23C

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Wall tiles damaged

105 CMR 451.123	Maintenance: Wall tiles dirty

Slop Sink Room # 23D

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

105 CMR 451.353	Interior Maintenance: Vent dirty and damaged

Shower # 23E

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Floor tiles missing

Closet # 23F

105 CMR 451.353	Interior Maintenance: Vent dirty

Shower # 23G

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Access panel rusted

105 CMR 451.123	Maintenance: Wall tiles missing

Shower # 23H

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123	Maintenance: Floor tiles missing near floor drain

Shower # 23J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Possible mold growth on ceiling

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Access panel rusted

105 CMR 451.123	Maintenance: Soap scum on wall tiles

Cells

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 1, 3, 9, 10, 15, 23, 24, 29, and 30

Unit 2-4

Common Area

105 CMR 451.353	Interior Maintenance: Window sills dirty near cell # 24

105 CMR 451.353	Interior Maintenance: Vent dirty outside closet # 24G

105 CMR 451.353	Interior Maintenance: Stairway dirty

Kitchenette

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty, water 	fountain dirty

FC 4-602.12(B)	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

Shower # 24B

105 CMR 451.123*	Maintenance: Shower walls need re-grouting

105 CMR 451.123*	Maintenance: Possible mold growth and soap scum on wall tiles

105 CMR 451.123*	Maintenance: Door frame rusted

105 CMR 451.123	Maintenance: Step tiles missing

105 CMR 451.123	Maintenance: Ceiling vent dirty

Slop Sink Room # 24C

No Violations Noted

Shower # 24D

105 CMR 451.123*	Maintenance: Shower walls need re-grouting

105 CMR 451.123*	Maintenance: Light fixture rusted

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Shower head loose

105 CMR 451.123	Maintenance: Floor tiles dirty

105 CMR 451.123	Maintenance: Door frame rusted

105 CMR 451.123	Maintenance: Soap scum on wall tiles

Meeting Room # 24E

No Violations Noted

Shower # 24F

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Shower head loose

105 CMR 451.123	Maintenance: Soap scum on walls tiles

Closet # 24G

105 CMR 451.350	Structural Maintenance: Wall damaged

Shower # 24H

105 CMR 451.123	Maintenance: Shower walls need re-grouting

105 CMR 451.123	Maintenance: Door frame rusted

105 CMR 451.123	Maintenance: Shower curtain missing

Shower # 24J

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Ceiling repair unfinished

105 CMR 451.123*	Maintenance: Door frame rusted

105 CMR 451.123*	Maintenance: Soap scum on wall tiles

Cells

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated milk 	observed in cell # 11, 15, 16, 18, 21, 25, 30, 32, 35 and 37

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Potentially	hazardous food not held at the proper cold holding temperature, unrefrigerated hard 	boiled egg observed in cell # 10

Entry Level (Inside)

Staff Cafeteria # 1066

FC 3-304.14(B)(2)*	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket

FC 4-601.11(A)	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, nozzles on 	juice machine dirty

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, tiles on counter

top damaged

FC 7-206.12*	Poisonous or Toxic Materials; Pesticides: Rodent traps not covered and tamper 	resistant

Weight Room # 1070

105 CMR 451.350	Structural Maintenance: Ceiling tiles damaged

Slop Sink Room # 1072

105 CMR 451.353	Interior Maintenance: Vent dirty

105 CMR 451.353	Interior Maintenance: No light shield provided in maintenance area

Water Fountain

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, leaking on floor

Blue Shirt’s Locker Room # 1075

105 CMR 451.123	Maintenance: Floor dirty

105 CMR 451.123*	Maintenance: Counter top damaged and not easily cleanable

105 CMR 451.123	Maintenance: Ceiling vents dirty

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, sink # 2 leaking

Female Staff Locker Room # 1076

105 CMR 451.123	Maintenance: Ceiling vents dirty

Captain and Lieutenants’ Locker Room # 1077

105 CMR 451.123	Maintenance: Ceiling vent dirty

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 440F

Shift Commanders Area

No Violations Noted

Administration Bathrooms

Female Bathroom # 1013

No Violations Noted

Male Bathroom # 1015

105 CMR 451.123	Maintenance: Front edge of counter top missing

Ground Level

Canteen Area # G10

105 CMR 451.353	Interior Maintenance: No light shield provided in maintenance area

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, light not working properly in refrigerator unit

Storage Room # G11

105 CMR 451.344	Illumination in Habitable Areas: Light fixtures not working properly

Maintenance # G12

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet leaking in bathroom

105 CMR 451.353	Interior Maintenance: No light shield provided in maintenance area

FC 3-302.11(A)(4)	Preventing Food and Ingredient Contamination: Preventing cross contamination, sugar	not appropriately covered

Locker Room # G13

No Violations Noted

Laundry Room # G23

No Violations Noted

Loading Dock # G26

FC 4-102.11(B)(2)	Materials for Construction and Repair; Multiuse: Unused single-service article not 	protected against contamination, utensils uncovered

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, gasket damaged

Garbage Room # G37

105 CMR 451.353	Interior Maintenance: Walls no longer easily cleanable, wall paint damaged

Staff Bathroom # G44

105 CMR 451.123	Maintenance: Ceiling vent dirty

Staff Bathroom # G46

No Violations Noted

Female Booking Area

Holding Cells

105 CMR 451.353	Interior Maintenance: Ceiling dirty in holding cell # 1

105 CMR 451.353	Interior Maintenance: Wall dirty in holding cell # 3

105 CMR 451.353	Interior Maintenance: Vent dirty in holding cell # 2, 3, and 4

105 CMR 451.353	Interior Maintenance: Flying insect observed in holding cell # 3

Bathroom # G54

105 CMR 451.110(A)*	Hygiene Supplies at Toilet and Handwash Sink: No soap at handwash sink

105 CMR 451.110(A)*	Hygiene Supplies at Toilet and Handwash Sink: No paper towels at handwash sink

105 CMR 451.110(B)	Hygiene Supplies at Toilet and Handwash Sink: No waste receptacle at handwash sink

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123*	Maintenance: Wall dirty

Locker Room # G55

No Violations Noted

Male Booking Area

Control

No Violations Noted

Property Room G62

105 CMR 451.123	Maintenance: Ceiling vent dirty in shower area

Staff Bathroom # G64

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No paper towels at handwash sink

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No soap at handwash sink

Male Intake Cell # G74

No Violations Noted

Holding Cage

No Violations Noted

Holding Cells

105 CMR 451.353*	Interior Maintenance: Light fixture dirty in holding cell # 1, 2, 4, and 5

Vehicle Trap # G75

105 CMR 451.353*	Interior Maintenance: Light shield missing and broken

Back Gate Control # G80

105 CMR 451.350	Structural Maintenance: Window damaged

FC 4-102.11(B)(2)	Materials for Construction and Repair; Multiuse: Unused single-service article not 	protected against contamination, utensils not stored handles up

Staff Bathroom # G81

No Violations Noted

Food Service Area

Oven and Steamer Hood Area

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not properly cleaned, light cage dirty

Grill Top Hood Area

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not properly cleaned, light cage dirty

Dry Storage

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, fire retardant 	coating on ceiling loose

FC 6-501.111(B)	Maintenance and Operations; Pest Control: Flying insects observed in dry storage area

FC 7-206.12	Poisonous or Toxic Materials; Pesticides: Rodent traps not covered and tamper 	resistant

Storage Cage

FC 6-501.111(B)	Maintenance and Operations; Pest Control: Pest population not controlled properly, 	rodent receive observed all along the wall ledge and behind the cabinet

Inmate Dinning Area

No Violation Noted

Inmate Bathroom

FC 6-202.14	Design, Construction, and Installation; Functionality: Toilet room not completely 	enclosed, door propped open

FC 6-501.111(B)	Maintenance and Operations; Pest Control: Flying insects observed in bathroom area

Meat Cutter

FC 4-903.11(B)(2)*	Protection of Clean Items, Storing: Uncovered equipment not protected from 	contaminations, meat cutter left uncovered

Chemical Storage Cage

No Violation Noted

Can Opener Table

FC 4-601.11(A)	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, can 	opener cutting surface dirty

Ice Machine

No Violation Noted

Refrigerator # 1

No Violation Noted

Refrigerator # 2

No Violation Noted

Vegetable Chest # 3

No Violation Noted

Milk Chest # 4

No Violation Noted

Freezer # 5

No Violation Noted

Bread Refrigerator # 6

No Violation Noted

Tray Prep Area

FC 6-305.11(B)	Numbers and Capacities; Dressing Area and Lockers: Personal clothing items stored 	in inappropriate location

FC 6-501.114(A)	Maintenance and Operations; Maintaining Premises: Nonfunctional equipment not 	repaired or removed from premises, dirty Hobart Buffalo Chopper not functioning 	properly

Kettle Area

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, handwash sink leaking from pipe

FC 6-301.11	Numbers and Capacity; Handwashing Facilities: No soap at handwash sink

Mop Cage

No Violation Noted

3-Compartment Sink

FC 4-501.114(A)	Maintenance and Operation; Equipment: Chlorine Sanitizer solution tested less than 	recommended concentration, no indication of sanitizer in the sanitizer compartment

FC 4-501.18	Maintenance and Operation, Equipment: Sanitizing solution dirty

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, hot water handle leaking

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, cold water controls for rinse hose leaking

Mechanical Warewashing Area

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, rinse sink leaking

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, mechanical warewashing machine leaking in several areas causing an 	extensive amount of standing water on the floor

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor grout 	missing and floor tiles damaged

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, ceiling tile missing

Observations and Recommendations

- Recommend emptying unused toilet in storage room # 6504

- Please note the following documents have been provided to Anthony Domagala, Assistant Deputy Superintendent-Guidelines for Medial Waste Management at Secure Lockup Facilities and example of record-keeping log for medical or biological waste

This facility does not comply with the Department’s Regulations cited above. In accordance with 105 CMR 451.404, please indicate next to each entry on the inspection report a plan of correction. Said plan of correction must be submitted within 10 days of receipt of this letter and should detail the specific steps that will be taken and the date of expected compliance. The plan of correction should be submitted to my attention, at the address listed above.

To review the specific regulatory requirements please visit our website at www.mass.gov/dph/dcs and click on "Community Sanitation Regulations" (available in both PDF and RTF formats).

To review the Food Establishment regulations please visit the Food Protection website at www.mass.gov/dph/fpp and click on “Food Protection Regulations”. Then under “Retail” click “105 CMR 590.000 - State Sanitary Code Chapter X – Minimum Sanitation Standards for Food Establishments” and “1999 Food Code”.

This inspection report is signed and certified under the pains and penalties of perjury.

Sincerely,

Lauren Thomas

Environmental Health Inspector, CSP, BEH

cc:	Suzanne K. Condon, Associate Commissioner, Director, BEH

Steven Hughes, Director, CSP, BEH

JudyAnn Bigby, MD, Secretary, Executive Office of Health and Human Services

Harold W. Clarke, Commissioner, DOC

Eugene Sumpter, Superintendent

Angel Lopez, FS-EHSO

Boston Public Health Commission

Clerk, Massachusetts House of Representatives

Clerk, Massachusetts Senate

Mary Elizabeth Heffernan, EOPS