| # Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | TVOCs (ppm) | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background (outdoors) | 370 | ND | 57 | 23 | 10-15 |  | ND |  |  |  | Mostly Cloudy, cool |
| 5th Floor |  |  |  |  |  |  |  |  |  |  |  |
| 501 Mechanical Room | 554 | ND | 76 | 23 | 3 | 0 | ND | N |  |  |  |
| Electrical Room | 582 | ND | 73 | 23 | 3 | 0 | ND |  |  |  |  |
| 4th Floor |  |  |  |  |  |  |  |  |  |  |  |
| 423 | 518 | ND | 74 | 19 | 5 | 2 | ND | N | Y | N | DO |
| 420 | 518 | ND | 74 | 19 | 1 | 0 | ND | N | Y | N | Fan coil unit, DO |
| 416A | 549 | ND | 74 | 19 | 2 | 1 | ND | N | Y | Y | DO |
| Reg of Deeds (ROD) Receptionist | 498 | ND | 73 | 19 | 2 | 2 | ND | N | Y | Y | DO |
| ROD 407 | 470 | ND | 73 | 20 | 2 | 0 | ND | N | Y | Y | Dust/debris on vents, AP-filter light on |
| ROD 3018-3066 | 440 | ND | 73 | 21 | 1 | 1 | ND | N | Y | Y |  |
| ROD 6332-6478 | 448 | ND | 73 | 20 | 1 | 0 | ND | N | Y | Y |  |
| Administration | 485 | ND | 73 | 22 | 2 | 2 | ND | N | Y | Y |  |
| HR | 462 | ND | 72 | 23 | 1 | 0 | ND | N | N | N | Old/soiled carpet, PF, CF |
| 401 | 455 | ND | 72 | 24 | 3 | 0 | ND | N | Y | Y | Interior window open, AP |
| 402 | 448 | ND | 72 | 24 | 1 | 0 | ND | N | Y | Y |  |
| 403 | 448 | ND | 73 | 22 | 2 | 0 | ND | N | Y | Y | WD CT, CF |
| 403A | 529 | ND | 74 | 23 | 2 | 0 | ND | N | Y | Y | Computer equipment |
| 403B | 449 | ND | 71 | 21 | 2 | 2 | ND | N | Y | Y | Wall mounted ACs |
| Publication Research Area | 490 | ND | 72 | 21 | 2 | 2 | ND | N | Y | Y |  |
| 412 | 471 | ND | 72 | 20 | 7 | 1 | ND | N | Y | Y |  |
| Land Court | 482 | ND | 73 | 20 | 2 | 2 | ND | N | Y | Y |  |
| Archive Area | 424 | ND | 73 | 18 | 2 | 0 | ND | N | Y | Y | Dehumidifier |
| 415 | 465 | ND | 72 | 21 | 7 | 0 | ND | N | Y Blocked | Y |  |
| 413 | 507 | ND | 72 | 22 | 2 | 0 | ND | N | Y | Y | AT-wiring, dehumidifier (full) |
| 412 | 462 | ND | 74 | 19 | 5 | 0 | ND | N | Y | Y | Large printer-heat, portable AC-ducted, PF, CF |
| 411 | 456 | ND | 72 | 20 | 3 | 1 | ND | N | Y | Y | PC, CF, discolored CTs, poor temperature control reported, shield on vent/louvers |
| 409-410 | 479 | ND | 72 | 19 | 3 | 1 | ND | N | Y | Y | Dust/debris-vents, PF, CF, PC, AP |
| 408 | 525 | ND | 72 | 19 | 2 | 1 | ND | N | Y | Y | CF, carpeting |
| 408A | 513 | ND | 74 | 19 | 2 | 1 | ND | N | y | Y | PF, CF, carpeting |
| Front Desk Area | 490 | ND | 74 | 20 | 2 | 4 | ND | N | Y | Y | Carpeting |
| 417 Kitchen | 580 | ND | 72 | 21 | 2 | 0 | ND | N | Y | Y | Refrigerator gasket-stained/mold |
| Probate Courtroom 1 | 534 | ND | 72 | 22 | 10 | 0 | ND | N | y | Y | Carpeting |
| Probate Courtroom 3 | 527 | ND | 71 | 22 | 2 | 0 | ND | N | Y | Y | Carpeting, dust/debris-vents/wall near ceiling |
| Conference Room A | 447 | ND | 71 | 23 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents |
| Conference Room B | 566 | ND | 71 | 23 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents |
| 427 Employee Lounge | 630 | ND | 72 | 24 | 3 | 4 | ND | N | Y | Y | Dust/debris-vents, DO |
| 426 | 584 | ND | 72 | 22 | 2 | 1 | ND | N | Y | Y | Dust/debris-vents, DO, CF |
| Probate Court Room 2 | 531 | ND | 72 | 23 | 2 | 0 | ND | N | Y | Y | PF, carpeting |
| Probate Court Room 4 | 529 | ND | 72 | 23 | 1 | 0 | ND | N | Y | Y |  |
| Conference Room B | 516 | ND | 72 | 22 | 3 | 0 | ND | N | Y | Y | 8 WD CT, MT |
| Conference Room A | 504 | ND | 71 | 22 | 3 | 0 | ND | N | Y | Y |  |
| 428 | 583 | ND | 72 | 23 | 2 | 1 | ND | N | Y | Y | Carpet squares |
| 428A | 532 | ND | 72 | 22 | 3 | 0 | ND | N | Y | Y | 3 WD CT |
| 428B | 546 | ND | 73 | 21 | 2 | 0 | ND | N | Y | Y |  |
| Jury Pool | 471 | ND | 71 | 18 | 3 | 2 | ND | N | Y | Y | Dust/debris-vents, PF, carpet, plants |
| Jury Pool Rear | 470 | ND | 71 | 18 | 3 | 0 | ND | N | Y | Y | WD CTs, plants-leaking on countertop, dust/debris-vents |
| Registry of Probate (ROP) | 664 | ND | 71 | 22 | 3 | 8 | ND | N | Y | Y | AI, 6 WD CTs |
| Probate Work Area | 479 | ND | 72 | 20 | 2 | 9 | ND | N | Y | Y | Dust/debris-vents/CTs, PF, PC, 15+ WD CTs |
| Vault | 447 | ND | 70 | 25 | 3 | 2 | ND | N | Y | Y | Missing vents, dust/debris-vents, 10+ WD CTs |
| 435 | 425 | ND | 69 | 21 | 3 | 0 | ND | N | Y | Y |  |
| 434 | 420 | ND | 69 | 20 | 3 | 0 | ND | N | Y | Y | PF, dust/debris-vents |
| 432 | 441 | ND | 70 | 20 | 3 | 0 | ND | N | Y | Y | Plants, dust/debris-vents, carpet |
| 431 | 475 | ND | 71 | 22 | 2 | 1 | ND | N | Y | Y | Dust/debris-vents, carpeting, plants |
| 431A | 452 | ND | 71 | 19 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents |
| 422 | 523 | ND | 73 | 18 | 3 | 0 | ND | N | Y | Y | Carpet tile |
| 421 | 480 | ND | 72 | 17 | 3 | 0 | ND | N | Y | Y |  |
| 419 | 514 | ND | 72 | 19 | 4 | 0 | ND | N | Y | Y | Plants |
| Reception-judges lobbies | 536 | ND | 72 | 19 | 3 | 2 | ND | N | Y | Y | Plants, AF |
| 416B | 607 | ND | 72 | 19 | 4 | O | ND | N | Y | Y | Plants |
| 3rd Floor |  |  |  |  |  |  |  |  |  |  |  |
| 320A | 601 | ND | 73 | 23 | 2 | 0 | ND | N | Y | Y | Plants, WD CTs x 2 |
| 320 reception | 599 | ND | 74 | 21 | 2 | 0 | ND | N | Y | Y |  |
| 320B | 604 | ND | 74 | 21 | 1 | 0 | ND | N | Y | Y | WD CT |
| 317 | 597 | ND | 74 | 22 | 2 | 1 | ND | N | Y | Y |  |
| 317B | 620 | ND | 74 | 21 | 3 | 1 | ND | N | Y | Y | Plants |
| 317A | 553 | ND | 73 | 20 | 3 | 0 | ND | N | Y | Y | Renovations |
| 315 | 550 | ND | 74 | 19 | 4 | 0 | ND | N | Y | Y | Personal heaters |
| Jury Room B | 639 | ND | 72 | 22 | 3 | 0 | ND | N | Y | Y |  |
| Jury Room A | 549 | ND | 72 | 21 | 1 | 0 | ND | N | Y | Y | WD CT |
| 313A | 594 | ND | 71 | 25 | 4 | 2 | ND | N | Y | Y |  |
| Court Room 3 | 604 | ND | 71 | 23 | 4 | 0 | ND | N | Y | Y |  |
| Law Library-front | 606 | ND | 73 | 25 | 3 | 3 | ND | N | Y | Y |  |
| Training Room | 569 | ND | 73 | 20 | 3 | 0 | ND | N | Y | Y | Newly renovated |
| 309 | 638 | ND | 75 | 26 | 3 | 0 | ND | N | Y | Y | Dust/debris on supply vent and ceiling |
| Library-rear | 582 | ND | 76 | 24 | 4 | 3 | ND | N | Y | Y | Broken window gaskets, missing ceiling tiles |
| Clerks- front | 596 | ND | 75 | 20 | 3 | 12 | ND | N | Y | Y | Carpet tile, DEM |
| Clerks- middle | 710 | ND | 75 | 22 | 4 | 12 | ND | N | Y | Y | HS, AF |
| 304 | 650 | ND | 74 | 22 | 3 | 1 | ND | N | Y | Y | Personal heater, plants |
| 302 | 643 | ND | 74 | 22 | 3 | 2 | ND | N | Y | Y | HS, AF, plants |
| 303 | 618 | ND | 73 | 22 | 3 | 1 | ND | N | Y | Y | AI, blocked fan coil vent |
| Superior-Clerks | 612 | ND | 73 | 21 | 5 | 5 | ND | N | Y | Y | Dusty vents/soot |
| Superior-Probation | 629 | ND | 73 | 22 | 4 | 7 | ND | N | Y | Y | Dusty vents |
| 338 | 665 | ND | 74 | 22 | 5 | 2 | ND | N | Y | Y | CPs |
| 339 | 725 | ND | 74 | 22 | 4 | 2 | ND | N | Y | Y | CPs |
| 343 | 655 | ND | 73 | 23 | 3 | 0 | ND | N | Y | Y | DEM |
| 344 | 677 | ND | 72 | 23 | 4 | 0 | ND | N | Y | Y |  |
| 341 | 677 | ND | 72 | 23 | 3 | 1 | ND | N | Y | Y |  |
| 346 | 719 | ND | 72 | 27 | 3 | 2 | ND | N | Y | Y | NC |
| 337 | 784 | ND | 73 | 26 | 4 | 2 | ND | N | Y | Y |  |
| 340 | 661 | ND | 72 | 24 | 4 | 1 | ND | N | Y | Y | PF |
| 342 | 656 | ND | 72 | 23 | 3 | 0 | ND | N | Y | Y | HS |
| Courtroom 6 | 541 | ND | 72 | 21 | 2 | 0 | ND | N | Y | Y |  |
| Courtroom 5 | 524 | ND | 72 | 21 | 1 | 0 | ND | N | Y | Y |  |
| Jury Room | 549 | ND | 73 | 20 | 2 | 1 | ND | N | Y | Y |  |
| Courtroom 2 | 539 | ND | 73 | 20 | 2 | 12 | ND | N | Y | Y |  |
| Courtroom 1 | 511 | ND | 72 | 20 | 1 | 0 | ND | N | Y | Y |  |
| 347A | 559 | ND | 73 | 20 | 2 | 1 | ND | N | Y | Y |  |
| 347 | 759 | ND | 74 | 20 | 2 | 0 | ND | N | Y | Y |  |
| Jury C | 492 | ND | 74 | 18 | 3 | 0 | ND | N | Y | Y |  |
| Jury D | 504 | ND | 73 | 18 | 4 | 0 | ND | N | Y | Y |  |
| DA- front | 570 | ND | 73 | 20 | 4 | 4 | ND | N | Y | Y |  |
| 350 | 529 | ND | 74 | 20 | 2 | 0 | ND | N | Y | Y | AI |
| 351 | 544 | ND | 74 | 20 | 1 | 0 | ND | N | Y | Y | DEM, HS, carpet |
| 352 | 547 | ND | 73 | 20 | 2 | 0 | ND | N | Y | Y |  |
| 358 | 581 | ND | 73 | 19 | 3 | 0 | ND | N | Y | Y | MT, dusty vents |
| 359 | 542 | ND | 73 | 20 | 1 | 0 | ND | N | Y | Y | AI |
| 353 | 557 | ND | 73 | 20 | 3 | 0 | ND | N | Y | Y | HS |
| 360 | 530 | ND | 73 | 20 | 1 | 0 | ND | N | Y | Y | Holes/pathways |
| 354 | 519 | ND | 72 | 19 | 2 | 0 | ND | N | Y | Y | HS |
| Break | 614 | ND | 73 | 20 | 3 | 4 | ND | N | Y | Y |  |
| 361 | 505 | ND | 73 | 21 | 3 | 0 | ND | N | Y | Y |  |
| 366 main | 510 | ND | 73 | 19 | 1 | 0 | ND | N | Y | Y |  |
| 369 | 500 | ND | 72 | 20 | 1 | 0 | ND | N | Y | Y |  |
| 368 | 509 | ND | 72 | 19 | 2 | 0 | ND | N | Y | Y | Carpet |
| 367 | 516 | ND | 73 | 20 | 2 | 0 | ND | N | Y | Y | AI, HS, plants |
| Rear corner | 510 | ND | 73 | 19 | 3 | 0 | ND | N | Y | Y |  |
| 2nd Floor |  |  |  |  |  |  |  |  |  |  |  |
| 242 | 474 | ND | 70 | 22 | 3 | 0 | ND | N | Y | Y | Dust/debris-vents/CT, WD CTs |
| 244 | 523 | ND | 70 | 22 | 3 | 0 | ND | N | Y | Y | Dust/debris-vents/CT, plants |
| 241 | 496 | ND | 69 | 22 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents |
| 241A | 494 | ND | 69 | 23 | 3 | 0 | ND | N | Y | Y |  |
| District Courtroom 10 | 458 | ND | 71 | 21 | 2 | 0 | ND | N | Y | Y |  |
| District Courtroom 9 | 452 | ND | 72 | 20 | 2 | 2 | ND | N | Y | Y |  |
| G48 | 440 | ND | 70 | 24 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents |
| Superior Courtroom 8 | 451 | ND | 72 | 20 | 2 | 0 | ND | N | Y | Y |  |
| Superior Courtroom 7 | 506 | ND | 72 | 20 | 2 | 0 | ND | N | Y | Y |  |
| District Courtroom 3 | 444 | ND | 72 | 20 | 2 | 0 | ND | N | Y | Y |  |
| District Courtroom 5 | 441 | ND | 72 | 20 | 3 | 0 | ND | N | Y | Y |  |
| District Courtroom 6 | 444 | ND | 72 | 20 | 2 | 0 | ND | N | Y | Y |  |
| 228 Lounge | 533 | ND | 73 | 21 | 2 | 3 | ND | N | Y | Y |  |
| 210A | 515 | ND | 74 | 19 | 2 | 1 | ND | N | Y | Y |  |
| 210 | 501 | ND | 74 | 18 | 2 | 1 | ND | N | Y | Y | HS, plants |
| 209 | 486 | ND | 74 | 18 | 2 | 0 | ND | N | Y | Y | Plants, WD CT |
| 208 | 468 | ND | 73 | 19 | 3 | 0 | ND | N | Y | Y | Dusty vent |
| 207 main | 482 | ND | 72 | 20 | 1 | 0 | ND | N | Y | Y | HS |
| Lobby B | 494 | ND | 73 | 21 | 1 | 0 | ND | N | Y | Y | Carpet, WD CT near window |
| Lobby A | 543 | ND | 73 | 22 | 2 | 1 | ND | N | Y | Y | Plants |
| 206 | 523 | ND | 73 | 20 | 3 | 0 | ND | N | Y | Y |  |
| 205 | 525 | ND | 72 | 20 | 4 | 1 | ND | N | Y | Y |  |
| 204 | 514 | ND | 72 | 21 | 3 | 0 | ND | N | Y | Y | Plants, HS |
| Lobby B | 527 | ND | 72 | 21 | 1 | 0 | ND | N | Y | Y | Plants |
| Lobby A | 529 | ND | 72 | 22 | 2 | 1 | ND | N | Y | Y | WD CTs |
| 246C | 501 | ND | 70 | 21 | 2 | 0 | ND | N | Y | Y | Plant |
| 246 | 519 | ND | 69 | 21 | 2 | 0 | ND | N | Y | Y | Soiled carpet |
| 246E | 545 | ND | 70 | 22 | 3 | 1 | ND | N | Y | Y | Missing ceiling tile |
| Jury | 499 | ND | 72 | 19 | 4 | 0 | ND | N | Y | Y | WD (buckets near window) |
| 249A | 510 | ND | 73 | 19 | 3 | 1 | ND | N | Y | Y | Missing CT, carpet stained |
| 249 | 505 | ND | 72 | 19 | 7 | 1 | ND | N | Y | Y | Old, soiled/torn carpet |
| Lobby B | 516 | ND | 72 | 19 | 10 | 1 | ND | N | Y | Y | WD CT (painted over) |
| 250 | 554 | ND | 72 | 20 | 4 | 0 | ND | N | Y | Y | Vacant |
| Director security | 509 | ND | 73 | 19 | 3 | 1 | ND | N | Y | Y | AI |
| Chief court officer | 543 | ND | 72 | 19 | 3 | 1 | ND | N | Y | Y | WD CT |
| 230 | 476 | ND | 71 | 19 | 3 | 0 | ND | N | Y | Y | Old lockup now storage |
| Small claims | 495 | ND | 72 | 20 | 3 | 9 | ND | N | Y | Y | Photocopier, HS |
| 214 | 511 | ND | 72 | 19 | 3 | 0 | ND | N | Y | N |  |
| 215 | 531 | ND | 72 | 20 | 3 | 0 | ND | N | Y | Y |  |
| 213 | 533 | ND | 73 | 19 | 3 | 0 | ND | N | Y | Y |  |
| 211 | 626 | ND | 73 | 21 | 2 | 2 | ND | N | Y | Y |  |
| 1st Floor |  |  |  |  |  |  |  |  |  |  |  |
| 121 | 480 | ND | 71 | 21 | 2 | 0 | ND | N | Y | Y | Carpeting |
| 121A | 484 | ND | 72 | 22 | 2 | 0 | ND | N | Y | Y | 4 WD CT, Dust/debris-vents/CTs |
| 121B | 488 | ND | 72 | 21 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents/CTs, plants, 2 WD CTs |
| Police Room | 530 | ND | 71 | 21 | 3 | 3 | ND | N | Y | Y | Dust/debris-vents/CTs |
| 109 | 522 | ND | 72 | 22 | 2 | 0 | ND | N | Y | Y | PC |
| DC Clerk Criminal | 508 | ND | 73 | 23 | 4 | 9 | ND | N | Y | Y | PC |
| 104 | 515 | ND | 73 | 22 | 2 | 0 | ND | N | Y | Y |  |
| 103 | 529 | ND | 72 | 22 | 3 | 0 | ND | N | Y | Y |  |
| 102 | 601 | ND | 74 | 24 | 2 | 0 | ND | N | Y | Y | Plug-in AF |
| Cash Office | 663 | ND | 75 | 22 | 2 | 4 | ND | N | Y | Y | Carpeting, plants |
| 108 | 503 | ND | 74 | 19 | 3 | 0 | ND | N | Y | Y | Dust/debris-vents/CTs |
| Prosecutor Main Work Area | 675 | ND | 72 | 22 | 2 | 3 | ND | N | Y | Y | CF |
| 115 | 530 | ND | 72 | 21 | 8 | 0 | ND | N | Y | Y | Dust/debris-vents/CTs |
| 116 | 509 | ND | 72 | 21 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents/CTs, carpeting |
| 117 | 491 | ND | 72 | 20 | 5 | 0 | ND | N | Y | Y | Dust/debris-vents/CTs, carpeting |
| 119 | 496 | ND | 72 | 21 | 5 | 0 | ND | N | Y | Y | Dust/debris-vents/CTs |
| 120 | 493 | ND | 72 | 21 | 2 | 3 | ND | N | Y | Y | Dust/debris-vents/CTs, carpeting |
| 114 | 582 | ND | 72 | 21 | 2 | 3 | ND | N | Y | Y | Dust/debris-vents |
| 138 | 577 | ND | 72 | 22 | 2 | 0 | ND | N | Y | Y | CF |
| Bar Association Lounge | 590 | ND | 72 | 23 | 4 | 5 | ND | N | Y | Y | Dust/debris-vents/CTs |
| 137 | 600 | ND | 73 | 23 | 1 | 3 | ND | N | Y | Y | Dust/debris-vents/CTs |
| 138 | 540 | ND | 72 | 22 | 2 | 0 | ND | N | Y | Y | Dust/debris-vents, carpet, WD CT |
| 135 | 536 | ND | 72 | 21 | 2 | 1 | ND | N | Y | Y | Dust/debris-vents, WD CTs, carpet |
| 167 | 519 | ND | 73 | 21 | 3 | 7 | ND | N | Y | Y | Dust/debris-vents, carpet squares |
| 145 | 479 | ND | 73 | 20 | 2 | 0 | ND | N | Y | Y |  |
| 146 | 525 | ND | 75 | 21 | 3 | 1 | ND | N | Y | Y |  |
| 147 | 563 | ND | 74 | 22 | 20 | 1 | ND | N | Y | Y | 3 WD CTs, AF odors |
| 148 | 537 | ND | 74 | 19 | 3 | 0 | ND | N | Y | Y | Plants |
| 149 | 470 | ND | 73 | 19 | 3 | 0 | ND | N | Y | Y | Plants, dust/debris-vents/CTs |
| 150 | 562 | ND | 73 | 20 | 3 | 2 | ND |  |  |  |  |
| 151 | 537 | ND | 74 | 19 | 2 | 1 | ND | N | Y | Y | Plants |
| 152 | 508 | ND | 74 | 20 | 4 | 0 | ND | N | Y | Y |  |
| 153 | 528 | ND | 75 | 18 | 3 | 1 | ND | N | Y | Y | Loose vent |
| 143 | 577 | ND | 75 | 19 | 3 | 3 | ND | N | Y | Y | Dust/debris-vents |
| 155 | 511 | ND | 75 | 19 | 6 | 0 | ND | N | Y | Y | WD CT |
| 156 | 514 | ND | 74 | 18 | 5 | 0 | ND | N | Y | Y |  |
| Break Area | 523 | ND | 75 | 19 | 4 | 1 | ND | N | Y | Y |  |
| 160 | 495 | ND | 76 | 17 | 4 | 0 | ND | N | Y | Y |  |
| 159 | 545 | ND | 75 | 19 | 4 | 1 | ND | N | Y | Y | Dust/debris-vents |
| 158 | 443 | ND | 75 | 17 | 3 | 0 | ND | N | Y | Y | Dust/debris-vents/cobwebs |
| 157 | 550 | ND | 75 | 20 | 4 | 1 | ND | N | Y | Y |  |
| 142 | 487 | ND | 75 | 18 | 3 | 2 | ND | N | Y | Y | Dust/debris-vents |
| 141 | 450 | ND | 75 | 17 | 3 | 0 | ND | N | Y | Y |  |
| 161 | 507 | ND | 75 | 18 | 3 | 2 | ND | N | Y | Y |  |
| 164 | 536 | ND | 75 | 17 | 3 | 0 | ND | N | Y | Y |  |
| 163 | 661 | ND | 75 | 17 | 7 | 0 | ND | N | Y | Y | Dust/debris-vents/CT |
| 166 | 470 | ND | 75 | 17 | 4 | 0 | ND | N | Y | Y | Dust/debris-vents/CT |
| 165 | 525 | ND | 75 | 18 | 3 | 1 | ND | N | Y | Y | Dust/debris-vents |
| 140 | 569 | ND | 75 | 18 | 5 | 2 | ND | N | Y | Y | Dust/debris-vents |
| 138 | 463 | ND | 75 | 17 | 3 | 1 | ND | N | Y | Y | Dust/debris-vents, WD CT |
| 131 | 527 | ND | 74 | 19 | 2 | 1 | ND | N | Y | Y |  |
| District Courtroom 2 | 462 | ND | 74 | 18 | 3 | 2 | ND | N | Y | Y |  |
| Main Lobby | 478 | ND | 71 | 19 | 4 | 15 | ND | N | Y | Y |  |

| # Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | TVOCs (ppm) | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background (outdoors) | 470 | ND | 54 | 78 | 44 | - | ND | - | - | - |  |
| District Courtroom 1 | 520 | ND | 73 | 45 | 3 | 0 | ND | N | Y | Y | Dust/debris-vents |
| District Courtroom 4 | 514 | ND | 72 | 46 | 3 | 0 | ND | N | Y | Y |  |
| Conference Room A | 533 | ND | 73 | 45 | 5 | 0 | ND | N | Y | Y | Dust/debris-vents |
| Conference Room B | 504 | ND | 72 | 46 | 3 | 6 | ND | N | Y | Y |  |
| Wood Shop | 672 | ND | 67 | 51 | 19 | 4 | ND | N | Y | N | DIY large particulate wood dust filter (recirculates only) |

| Location | Mercury Level (µg/m3) |
| --- | --- |
| Background (outdoors) | 0.019 |
| 4th Floor |  |
| 422 | 0.007 |
| 421 | 0.010 |
| 420 | 0.010 |
| 419 | 0.011 |
| 4th floor elevator lobby | 0.012 |
| 428 | 0.011 |
| 428 R | 0.012 |
| 428 L | 0.010 |
| 430 | 0.011 |
| Jury Pool | 0.013-0.015 |
| Probate Court 4 | 0.014 |
| Probate reception | 0.016 |
| Probate vault | 0.002-0.009 |
| 439 | 0.003 |
| 437 | 0.004 |
| 435 | 0.005 |
| 431 A | 0.009 |
| 434 | 0.013 |
| 433 | 0.013 |
| 432 | 0.013 |
| 431 | 0.012 |
| Main lobby | 0.010-0.014 |
| Deed reception | 0.013 |
| 407 | 0.013 |
| Deeds stacks | 0.009-0.012 |
| Deeds front desk | 0.009-0.011 |
| Deeds printer | 0.010 |
| Deeds corner office | 0.010 |
| 403 | 0.009 |
| 404 | 0.008 |
| 408A | 0.010 |
| 406 | 0.011 |
| 409 | 0.009 |
| 411 | 0.012 |
| Deeds recorder | 0.009 |
| 412 | 0.009 |
| 413 | 0.009 |
| Deeds archives | 0.009 |
| 402 | 0.007 |
| 401 | 0.006 |
| Deeds breakroom | 0.010 |
| 3rd Floor |  |
| 331 | 0.010 |
| 347B | 0.010 |
| 347 | 0.010 |
| 347A | 0.011 |
| 348 | 0.009 |
| 320 A | 0.010 |
| 320 B | 0.010 |
| 320 | 0.009 |
| 3rd floor elevator lobby | 0.010 |
| 3rd floor lock up | 0.009 |
| 330 | 0.007 |
| 334 | 0.008 |
| DA reception | 0.011 |
| DA office | 0.008 |
| DA assistant | 0.008 |
| 366 | 0.008 |
| DA office | 0.010 |
| 361 | 0.011 |
| 368 | 0.009 |
| 369 | 0.010 |
| 361 | 0.009 |
| 363 | 0.008 |
| 362 | 0.007 |
| 364 | 0.007 |
| 367 | 0.009 |
| 365 | 0.010 |
| 373 | 0.009 |
| 372 | 0.007 |
| 371 | 0.002 |
| DA break room | 0.006 |
| 360 | 0.008 |
| 354 | 0.008 |
| 353 | 0.010 |
| 359 | 0.009 |
| 358 | 0.008 |
| 352 | 0.009 |
| 351 | 0.009 |
| 356 | 0.007 |
| 350 | 0.008 |
| 350 A | 0.009 |
| 336 | 0.007 |
| 337 | 0.008 |
| 346 | 0.004 |
| 342 | 0.007 |
| 341 | 0.008 |
| 305 | 0.007 |
| 302 | 0.009 |
| 310 | 0.008 |
| 309 | 0.007 |
| Probation reception | 0.010 |
| Probation main desk | 0.009 |
| 342 | 0.005 |
| 345 | 0.007 |
| 344 | 0.005 |
| 343 | 0.006 |
| 339 | 0.006 |
| 340 | 0.006 |
| 302 | 0.008 |
| 303 | 0.007 |
| 304 | 0.005 |
| Superior Clerk Civil | 0.009 |
| Superior Clerk Criminal | 0.009 |
| Library | 0.007 |
| 320 A | 0.009 |
| 320 B | 0.009 |
| 320 | 0.009 |
| 317 B | 0.010 |
| 317 A | 0.009 |
| 317 | 0.008 |
| 315 | 0.007 |
| 3rd floor jury room B | 0.009 |
| 2nd Floor |  |
| District Clerk of Court reception | 0.010 |
| District Clerk of Court main office | 0.009 |
| 211 | 0.009 |
| District Clerk of Court | 0.010 |
| 228 | 0.009 |
| 213 | 0.010 |
| 212 | 0.011 |
| 215 | 0.011 |
| District Clerk of Court vault | 0.008 |
| District Clerk of Court conference room | 0.008 |
| 218 | 0.010 |
| 219 | 0.009 |
| 214 | 0.007 |
| 230 | 0.009 |
| Court office | 0.010 |
| Director of Security HCBA | 0.010 |
| 246 C | 0.010 |
| 246 | 0.010 |
| 249 A | 0.010 |
| 249 B | 0.011 |
| 210A | 0.002 |
| 210 | 0.002 |
| 209 | 0.003 |
| 208 | 0.002 |
| 204 A | 0.005 |
| 204 | 0.002 |
| 204 B | 0.004 |
| 205 | 0.003 |
| 207 A | 0.002 |
| 207 | 0.002 |
| 207 B | 0.003 |
| 1st Floor |  |
| Main lobby | 0.008 |
| District Court cash office | 0.010 |
| 105 | 0.010 |
| 107 | 0.008 |
| 102 | 0.007 |
| 103 | 0.006 |
| 104 | 0.007 |
| 111 | 0.006 |
| District Court criminal clerk | 0.006 |
| 108 | 0.007 |
| 109 | 0.007 |
| Break room | 0.007 |
| Clerk of Court office | 0.009 |
| 101 | 0.006 |
| 198 A | 0.009 |
| Court service | 0.010 |
| 124 | 0.009 |
| 140 | 0.010 |
| 140 A | 0.011 |
| 121 B | 0.010 |
| 121 | 0.009 |
| 121 A | 0.008 |
| District Court Probation | 0.011 |
| Probation Main Office | 0.009 |
| 143 | 0.008 |
| 145 | 0.007 |
| 146 | 0.007 |
| 147 | 0.008 |
| 148 | 0.007 |
| 149 | 0.009 |
| 150 | 0.009 |
| 151 | 0.009 |
| 152 | 0.010 |
| 153 | 0.010 |
| 157 | 0.009 |
| 154 | 0.008 |
| 158 | 0.009 |
| 155 | 0.008 |
| 159 | 0.008 |
| 156 | 0.007 |
| 160 | 0.007 |
| Lounge | 0.008 |
| 164 | 0.009 |
| 163 | 0.007 |
| 166 | 0.009 |
| 162 | 0.005 |
| Attorney lounge | 0.002 |
| 107 | 0.002 |
| DA office | 0.002 |
| DA office | 0.002 |
| 108A | 0.003 |
| 161 | 0.005 |
| 165 | 0.004 |
| 162 | 0.006 |
| DA Conference room | 0.002 |
| DA Main office | 0.002 |
| DA office | 0.002 |
| DA office | 0.002 |
| DA break room | 0.002 |
| 115 | 0.002 |
| 120 | 0.002 |
| 119 | 0.002 |
| 117 | 0.002 |
| 116 | 0.002 |
| Main Lobby security | 0.002 |
| Main Lobby Information desk | 0.003 |
| Court Sessions |  |
| DC court 4 | 0.003 |
| DC court 3 | 0.005 |
| DC court 5 | 0.005 |
| DC court 6 | 0.004 |
| DC court 1 | 0.004 |
| DC court 2 | 0.005 |
| DC court 7 | 0.004 |
| DC court 8 | 0.003 |
| DC court 9 | 0.003 |
| DC court 11 | 0.002 |
| SC court 2 | 0.005 |
| SC court 1 | 0.004 |
| SC court 4 | 0.004 |
| SC court 3 | 0.004 |
| SC court 5 | 0.003 |
| SC court 6 | 0.003 |
| Ground floor |  |
| G Snack Bar | 0.006 |
| G38 | 0.008 |

| HVAC component | Expected Service Life Defined by ASHRAE, | Current Age of equipment beyond ASHRAE service life (date of construction = 1973) | Percentage of Exceedance of Actual Service Life compared to ASHRAE service life |
| --- | --- | --- | --- |
| Fan coil unit | 20 | 45 | 225 % |
| Ductwork | 30 | 45 | 150 % |
| Dampers | 20 | 45 | 225 % |
| Insulation, molded | 20 | 45 | 225 % |
| Insulation blankets | 24 | 45 | 180 % |
| Controls electric | 16 | 45 | 280 % |
| Controls electronic | 15 | 45 | 300 % |
| Air terminals-diffusers, grilles and registers | 27 | 45 | 167 % |

Picture 1

View of Roderick Ireland Courthouse (RIC) from I-91

Picture 2

RIC

HJC

RIC and Housing-Juvenile Court (HJC)

Picture 3

Ground level HVAC system fresh air intake

Picture 4

Fresh air diffuser (Note discoloration on ceiling tiles)

Picture 5

Fan coil unit (FCU)

Picture 6

Condensation collector coated with scale

Picture 7

Corrosion on FCU motor cover, flexible steel electric conduit, and the underside of the drip pan

Picture 8

An uninsulated copper pipe beneath water-damaged fiberglass insulation

Picture 9

Frayed insulation on FCU cover

Picture 10

FCU filter medium that needs to be physically cut to size

Picture 11

Dust/debris/staining on vents and surrounding ceiling tiles

Picture 12

Dust/debris/staining on vents and surrounding ceiling tiles

Picture 13

Water-damaged ceiling tiles

Picture 14

Water-damaged ceiling tiles

Picture 15

Plant with leaking water on countertop

Expected service life with routine maintenance.  Service life can be reduced if equipment was not routinely maintained.

ASHRAE 1991 Applications Handbook, Table 3, page 33.3