| # Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | TVOCs (ppm) | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background (outdoors) | 470 | ND | 54 | 78 | 44 | - | ND | - | - | - | Light rain |
| Basement |  |  |  |  |  |  |  |  |  |  |  |
| B9 Utility | 756 | ND | 75 | 45 | 27 | 1 | ND | N | Y | Y | Dust/debris-vents |
| B10 | 773 | ND | 71 | 41 | 12 | 0 | ND | N | Y | Y | Dust/debris-vents |
| B11 | 852 | ND | 72 | 38 | 7 | 5 | ND | N | Y | Y | Dust/debris-vents/CTs, ATs |
| B14 | 613 | ND | 72 | 43 | 4 | 0 | ND | N | Y | Y | Air purifier |
| Utility/Records Storage | 737 | ND | 70 | 43 | 12 | 0 | ND | N | Y | Y |  |
| B17 | 770 | ND | 74 | 37 | 11 | 0 | ND | N | Y | Y | Air handling unit-moldy box/panel space |
| B21 | 780 | ND | 74 | 41 | 8 | 0 | ND | N | Y | Y | Soiled carpet/wrinkled |
| B22 | 773 | ND | 73 | 42 | 4 | 0 | ND | N | Y | N |  |
| B23 | 820 | ND | 71 | 44 | 4 | 0 | ND | N | Y | Y | Peeling paint, efflorescence wall, dust/debris-vents |
| B26 | 799 | ND | 72 | 44 | 4 | 0 | ND | N | Y | Y | Dust/debris-vents |
| B28 | 773 | ND | 74 | 43 | 5 | 1 | ND | N | Y | Y | Dust/debris-vents, carpet squares |
| B30 Conf Rm | 775 | ND | 72 | 43 | 5 | 0 | ND | N | Y | Y | Carpeting |
| B33 | 837 | ND | 73 | 43 | 4 | 1 | ND | N | Y | Y |  |
| B34 | 800 | ND | 72 | 44 | 4 | 0 | ND | N | Y | Y | Dust/debris-vents, carpeting |
| B35 | 767 | ND | 71 | 43 | 5 | 0 | ND | N | Y | Y | DO, carpeting |
| B36 | 780 | ND | 72 | 44 | 5 | 0 | ND | N | Y | Y | Carpeting |
| B37 | 870 | ND | 72 | 45 | 4 | 2 | ND | N | Y | Y | Carpeting, DO |
| B39 | 718 | ND | 69 | 32 | 3 | 0 | ND | N | Y | Y |  |
| B48 Hallway | 765 | ND | 71 | 33 | 4 | 0 | ND | N | Y | Y | Peeling paint, efflorescence wall |
| B58 | 777 | ND | 69 | 44 | 4 | 0 | ND | N | Y | Y | Chronic clogs reported-sewer line (odors), records storage, boxes on floor, AF |
| B61 | 742 | ND | 70 | 32 | 4 | 2 | ND | N | Y | Y |  |
| 1st Floor |  |  |  |  |  |  |  |  |  |  |  |
| Public Waiting area (1st floor) | 1304 | ND | 68 | 50 | 15 | 7 | ND | N | Y | Y |  |
| 151 | 1589 | ND | 70 | 46 | 16 | 3 | ND | N | Y | Y | Carpet |
| Conference B | 1505 | ND | 72 | 42 | 19 | 2 | ND | N | Y | N |  |
| 132 | 1137 | ND | 73 | 43 | 16 | 12 | ND | Y | Y | Y | Carpet, CPs, HS |
| 144 | 1061 | ND | 73 | 43 | 15 | 2 | ND | N | Y | Y | AI |
| 138 | 1053 | ND | 72 | 44 | 17 | 1 | ND | Y | Y | Y | Carpet |
| 137 | 1018 | ND | 72 | 44 | 15 | 0 | ND | Y | Y | Y | Heat pumps |
| 130 | 1006 | ND | 72 | 44 | 17 | 0 | ND | Y | Y | Y |  |
| 135 | 1166 | ND | 73 | 57 | 88* | 2 | 35-40* | Y | Y | Y | *Floor cleaning in progress |
| 126 | 924 | ND | 73 | 42 | 15 | 0 | ND | Y | Y | Y | Carpet |
| 102-Clerks | 1013 | ND | 74 | 44 | 15 | 11 | ND | Y | Y | Y | Carpet |
| 116 | 981 | ND | 75 | 43 | 14 | 0 | ND | Y | Y | Y | Plants |
| 101 | 1002 | ND | 75 | 43 | 15 | 2 | ND | Y | Y | Y | Carpet tile |
| 115 | 849 | ND | 76 | 41 | 14 | 1 | ND | Y | Y | Y | Carpet |
| Hall near 110 | 987 | ND | 76 | 41 | 14 | 1 | ND | Y | Y | Y |  |
| Courtroom 2 | 1151 | ND | 75 | 34 | 11 | 5 | ND | N | Y | Y |  |
| 120 | 1069 | ND | 75 | 35 | 8 | 0 | ND | Y | Y | Y | Carpet |
| Conference A | 1273 | ND | 72 | 37 | 9 | 0 | ND | N | Y | Y |  |
| 151 Hall | 1314 | ND | 72 | 37 | 7 | 0 | ND | N | Y | Y |  |
| Juvenile Foyer 150 Hall | 1218 | ND | 72 | 39 | 9 | 3 | ND | N | N | N |  |
| 123 Hall | 1223 | ND | 73 | 41 | 8 | 4 | ND | N | N | N | WD plaster ceiling |
| 106 Foyer | 1138 | ND | 74 | 37 | 10 | 5 | ND | N | N | N |  |
| 152 (Court) | 1591 | ND | 68 | 45 | 16 | session ended 5 min ago | ND | Y | Y | Y | Old, soiled carpet |
| 2nd Floor |  |  |  |  |  |  |  |  |  |  |  |
| Housing Court Lobby | 978 | ND | 73 | 45 | 8 | 3 | ND | N | Y | Y |  |
| Court Room 2 | 826 | ND | 72 | 41 | 8 | 0 | ND | N | Y | Y | Carpeting |
| 202 Judge’s Lobby | 897 | ND | 76 | 39 | 7 | 1 | ND | N | Y | N | Restroom-no exhaust |
| 208 | 910 | ND | 70 | 47 | 6 | 0 | ND | N | Y | Y | Peeling wallpaper, WD CT |
| 215 | 871 | ND | 68 | 47 | 6 | 0 | ND | N | Y | Y |  |
| 216 | 969 | ND | 76 | 38 | 5 | 1 | ND | N | Y | N |  |
| 220 | 869 | ND | 71 | 46 | 8 | 0 | ND | N | Y | Y |  |
| 235 | 690 | ND | 71 | 43 | 2 | 0 | ND | N | Y | Y | Carpeting |
| 243 | 1065 | ND | 73 | 39 | 8 | 0 | ND | N | Y | Y | HS |
| 242 | 930 | ND | 73 | 39 | 9 | 0 | ND | N | Y | Y | Non-ducted return |
| 241 | 1224 | ND | 73 | 40 | 7 | 0 | ND | Y | Y | Y | Plants |
| 249 | 1048 | ND | 72 | 42 | 6 | 1 | ND | Y | Y | Y | HS, AF |
| 250 | 894 | ND | 72 | 40 | 7 | 0 | ND | Y | Y | Y | Carpet |
| 251 | 1068 | ND | 71 | 44 | 9 | 1 | ND | Y | Y | Y | WD from units/roof |
| 252 | 1095 | ND | 71 | 43 | 10 | 1 | ND | Y | Y | Y | HS |
| 254 | 1052 | ND | 70 | 43 | 10 | 1 | ND | Y | Y | N | Plants, CP |
| 253 | 1144 | ND | 70 | 44 | 8 | 1 | ND | Y | Y | N | HS |
| 247 | 1101 | ND | 70 | 43 | 9 | 0 | ND | N | Y | N |  |
| 246 | 1044 | ND | 70 | 44 | 9 | 0 | ND | N | Y | N | Missing CT |
| 245 | 990 | ND | 71 | 42 | 8 | ND | ND | Y | Y | Y | Dusty vents |
| Hall outside 245 | - | - | - | - | - | - | - | - | - | - | WD CTs |
| 226 | 980 | ND | 72 | 41 | 7 | 0 | ND | N | Y | Y | HS |
| 223 | 922 | ND | 72 | 41 | 6 | 0 | ND | Y | Y | Y | Musty odor |
| 240 | 1119 | ND | 73 | 42 | 8 | 2 | ND | Y | Y | Y | HS |
| 227 | 1069 | ND | 73 | 41 | 8 | 1 | ND | N | Y | Y | HS, AI |
| 239 | - | - | - | - | - | - | - | - | - | - | Small unoccupied room w/fridge and old janitor sink, WD plaster, efflorescence |
| 232 | 993 | ND | 74 | 39 | 7 | 1 | ND | N | Y | Y | Old carpet, debris in vent |
| 222 (Courtroom 1) | 952 | ND | 72 | 45 | 12 | 1 | ND | N | Y | Y | WD ceilings |
| 3rd Floor |  |  |  |  |  |  |  |  |  |  |  |
| 328 | 1152 | ND | 74 | 38 | 7 | 4 | ND | N | Y | Y | Carpet |
| 323 | 1146 | ND | 73 | 37 | 6 | 2 | ND | Y | Y | Y |  |
| 324 | 1196 | ND | 73 | 39 | 7 | 0 | ND | N | Y | Y | WD CT, HS |
| 325 | 1147 | ND | 73 | 38 | 6 | 1 | ND | N | Y | Y | HS, personal heater |
| 326 | 1158 | ND | 74 | 38 | 7 | 0 | ND | Y | Y | Y | WD CT near return vent |
| 338 | 1098 | ND | 74 | 36 | 6 | 7 | ND | Y | Y | Y | Carpet |
| 344 Storage | - | - | - | - | - | - | - | - | - | - | WD |
| 339 File storage | - | - | - | - | - | - | - | - | - | - | Dusty vent |
| 346 | 1098 | ND | 73 | 37 | 7 | 1 | ND | Y | Y | Y | AF (reeds), WD CT |
| 347 | 991 | ND | 70 | 36 | 6 | 0 | ND | Y | Y | Y | WD CT |
| 342 | 968 | ND | 68 | 39 | 5 | 0 | ND | Y | Y dusty | Y | Electric baseboard |
| 341 | 1004 | ND | 67 | 40 | 5 | 0 | ND | Y | Y | Y | HS |
| 336 | 1036 | ND | 68 | 45 | 6 | 0 | ND | Y | Y | Y |  |
| 300 Conf Room | 741 | ND | 71 | 44 | 3 | 0 | ND | N | Y | Y | Carpeting |
| 301 | 873 | ND | 71 | 43 | 4 | 1 | ND | N | Y | Y | 4 WD CT, carpeting |
| 305 | 861 | ND | 71 | 44 | 2 | 0 | ND | N | Y | Y | Carpeting, plants |
| 307 Break Room | 854 | ND | 72 | 44 | 58* | 3 | ND | N | Y | Y | *Elevated PM2.5 from burnt food/toaster |
| 321 | 792 | ND | 71 | 43 | 3 | 0 | ND | N | Y | Y | Carpeting |
| 322 | 824 | ND | 71 | 44 | 9 | 1 | ND | N | Y | Y | Dust/debris-vents, DO, carpeting |

| Location | Mercury Level (µg/m3) |
| --- | --- |
| Background (outside) | 0.016 -0.019 |
| 337 | 0.118 |
| 336 | 0.100 |
| 348 | 0.081 |
| 340 | 0.121 |
| 342 | 0.122 |
| 343 | 0.125 |
| 341 | 0.112 |
| 330 | 0.121 |
| 334 | 0.122 |
| 347 | 0.120 |
| 338 | 0.124 |
| 328 | 0.131 |
| 323 | 0.130 |
| 324 | 0.127 |
| 325 | 0.125 |
| 326 | 0.119 |
| 252 | 0.108 |
| 245 | 0.102 |
| 254 | 0.108 |
| 247 | 0.109 |
| 253 | 0.106 |
| 251 | 0.102 |
| 244 | 0.108 |
| 250 | 0.105 |
| 242 | 0.103 |
| 240 | 0.122 |
| 227 | 0.117 |
| 239 | 0.118 |
| 249 | 0.101 |
| 155 | 0.261 |
| 151 | 0.213 |
| 151C | 0.322 |
| 151B | 0.341 |
| 151A | 0.336 |
| 124 | 0.188 |
| 132 | 0.080 |
| 144 | 0.074 |
| 142 | 0.073 |
| 138 | 0.077 |
| 137 | 0.076 |
| 130 | 0.076 |
| 136 | 0.078 |
| 135 | 0.080 |
| 126 | 0.069 |
| Juvenile Court Foyer | 0.155 |
| Housing Court Foyer | 0.069 |
| 116 | 0.054 |
| Housing Clerk | 0.056 |
| 101 | 0.053 |
| 115 | 0.024 |
| 119 | 0.151 |
| 215 | 0.059 |
| 220 | 0.053 |
| 235 | 0.052 |
| 227 | 0.077 |
| 226 | 0.088 |
| B47 | 0.422 |
| B57 | 0.426 |
| B46 | 0.228 |
| B39 | 2.755 |
| B39 B1 cell | 3.220 |
| B39 B2 cell | 1.350 |
| B39 B3 cell | 1.700 |
| B39 B4 cell | 1.510 |
| B39 interior room | 1.185 |
| B15 | 0.065 |
| B04 | 0.062 |
| B04 interior room | 0.066 |
| B15 | 0.067 |

| Location | Mercury Level (µg/m3) |
| --- | --- |
| Background (Outdoors) | 0.007 |
| Garage | 0.002 |
| B13 | 0.193 |
| B16 | 0.183 |
| B48 Hallway | 1.505 |
| B39 Cell Control | 2.137 |
| B39 B1 Cell | 6.378 |
| B39 B2 Cell | 2.078 |
| B39 B3 Cell | 0.658 |
| B39 B4 Cell | 0.948 |
| B39 Toilet | 0.922 |
| B46 Mechanical Room | 0.375 |
| B46 inside vent duct | 0.550 |
| B17 Mechanical Room | 0.112 |
| B17 inside vent duct | 0.115 |
| B47 | 0.444 |
| B61 | 0.526 |
| B61 A10 | 0.515 |
| B61 A09 | 0.560 |
| B61 A08 | 0.507 |
| B61 A07 | 0.527 |
| B61 A06 | 0.529 |
| B61 A05 | 0.505 |
| B61 A04 | 0.518 |
| B61 A03 | 0.527 |
| B61 A02 | 0.427 |
| B61 A01 | 0.541 |
| B51 elevator mechanical room | 1.568 |
| 151c | 0.411 |
| 151b | 0.453 |
| 151c | 0.403 |
| 155 | 0.310 |
| 124 | 0.224 |
| Elevator on 3rd floor | 0.500 |
| 3rd floor elevator foyer | 0.131 |
| Elevator on 2nd floor | 0.331 |
| 2nd floor elevator foyer | 0.122 |
| Elevator on 1st floor | 0.386 |
| 1st floor elevator foyer | 0.317 |
| Elevator on basement level | 0.376 |
| Basement elevator foyer | 1.505 |

Picture 1

Padding in B39 cell B1

Picture 2

Typical cell without padding

Picture 3

Close up of padding on floor of B39 cell B1

Picture 4

Elevator next to door to B39 (left)

Picture 5

Elevator pressure equalization vent in B50

Picture 6

Fresh air supply vent (arrow) in B39 B1

Picture 7

Water-damaged ceiling tiles

Picture 8

Water-damaged ceiling tile

Picture 9

Peeling paint and efflorescence on wall plaster

Picture 10

Peeling paint and efflorescence on wall plaster

Picture 11

Peeling paint and efflorescence on wall plaster

Picture 12

AHU missing its filter panel

Picture 13

Moldy/water-damaged box near AHU in Picture 12

Picture 14

Dust/debris accumulation on supply vent and surrounding ceiling tiles

Picture 15

Dust/debris accumulation on supply vent

Picture 16

Area in basement where sewer backups reportedly occur