Summary of Massachusetts

Drinking Water Program

Testing Requirements for Public Water Systems

This fact sheet summarizes drinking water testing requirements, maximum contaminant levels (MCLs), and Maximum Residual Disinfectant Levels (MRDLs) in the State of Massachusetts. These MCLs, MRDLs, and drinking water standards have been established by the U.S. Environmental Protection Agency or the State of Massachusetts for the protection of the public health.

These requirements apply to all public water systems in the state - systems serving drinking water to at least 25 individuals (or 15 service connections) at least 60 days of the year. There are two main types of public water systems:

•	Community Water Systems - primarily serve year-round residents; and

•	Non-Community Systems - serve water to non-residential customers and may include restaurants, factories, schools and hospitals.

Non-community systems that regularly serve at least 25 of the same people, for approximately four or more hours a day, four or more days per week, for more than six months or 180 days of the year are called Non-Transient Non-Community Water Systems (NTNCs) and are regulated more stringently than Transient Non-Community Water Systems (TNCs).

The standards listed apply to water, which is delivered to the user’s tap. Most samples are collected from the point of entry to the distribution system (after any treatment); however, some measurements including those for disinfectants, some disinfection byproducts (trihalomethanes and haloacetic acids), bacteria, lead and copper are conducted out in the distribution system. For lead and copper, the MCL has been replaced with an "action level" and is measured at the consumer’s tap.

Determining compliance with these standards differs with each contaminant. The regulations and the individual system's approved sampling plan must be consulted for more specific information. In certain cases, MassDEP may require more frequent testing than specified.

MassDEP also utilizes health-based guidance numbers for chemicals for which standards have not been established. These are determined by the MassDEP Office of Research and Standards (ORS) and applied on a case-by-case basis. The list of guidance values (ORSG) is updated periodically.

Also included is a list of the federal and state secondary contaminant levels. These are aesthetic standards but they may be enforced on a case by case basis.

Copies of the Massachusetts Drinking Water Regulations, 310 CMR 22.00, are available at http://www.mass.gov/dep/water/laws/regulati.htm#dw. If you have any questions on this information please contact the MassDEP Drinking Water Program at 617-292-5770, or Program.Director-DWP@state.ma.us.

Inorganic Compounds

| Parameter | CASRN* | # MCL | Monitoring Requirements |
| --- | --- | --- | --- |
| Antimony | 7440360 | 0.006 mg/l | Monitoring frequency depends on MassDEP-approved sampling plan. Community and non-transient non-community water supply sources monitoring frequency ranges from once per year for surface water sources to once every three years for groundwater sources. Non-vulnerable sources may be granted waivers and sample once every nine years. 1Statewide waivers have been approved by the U.S. EPA for source waters. 2There is also a secondary MCL for fluoride which is 2.0 mg/l. 3Transient Non-Community systems (TNC) are required to monitor for these contaminants. |
| Arsenic | 7440382 | 0.010 mg/l |  |
| Asbestos1 | 1332214 | 7 million fibers/l |  |
| Barium | 7440393 | 2 mg/l |  |
| Beryllium | 7440417 | 0.004 mg/l |  |
| Cadmium | 7440439 | 0.005 mg/l |  |
| Chromium | 7440473 | 0.1 mg/l |  |
| Cyanide | 57125 | 0.2 mg/l |  |
| Fluoride2 | 7782414 | 4 mg/l |  |
| Lead (action level) | 7439921 | 0.015 mg/l |  |
| Copper (action level) | 7440508 | 1.3 mg/l |  |
| Mercury | 7439976 | 0.002 mg/l |  |
| Nitrate (as N)3 | 14797558 | 10 mg/l |  |
| Nitrite (as N)3 | 14797650 | 1 mg/l |  |
| Total Nitrate & Nitrite (as N) | -- | 10 mg/l |  |
| Perchlorate | 14797730 | 0.0020 mg/l |  |
| Selenium | 7782492 | 0.05 mg/l |  |
| Thallium | 7440280 | 0.002 mg/l |  |

Volatile Organic Compounds

| Parameter | CASRN | # MCL | Monitoring Requirements |
| --- | --- | --- | --- |
| Benzene | 71432 | 0.005 mg/l | Monitoring frequency depends on MassDEP–approved sampling plan. Community and non-transient non-community water supply sources must initially monitor for four consecutive quarters every three years. Waivers may be granted to non-vulnerable sources to monitor once every three years. Monitoring for the following unregulated VOCs is also required: 5MTBE has an ORSG not an MCL |
| Carbon tetrachloride | 56235 | 0.005 mg/l |  |
| Dichloromethane | 75092 | 0.005 mg/l |  |
| 1,2-Dichlorobenzene (o-DCB) | 95501 | 0.6 mg/l |  |
| 1,4-Dichlorobenzene(P-DCB) | 106467 | 0.005 mg/l |  |
| 1,2-Dichloroethane | 107062 | 0.005 mg/l |  |
| 1,2-Dichloroethylene (cis) | 156592 | 0.07 mg/l |  |
| 1,2-Dichloroethylene (trans) | 156605 | 0.1 mg/l |  |
| 1,1-Dichloroethylene | 75354 | 0.007 mg/l |  |
| 1,2-Dichloropropane | 78875 | 0.005 mg/l |  |
| Ethylbenzene | 100414 | 0.7 mg/l |  |
| Methyl tert-Butyl Ether (MTBE)5 | 1634044 | 0.007 mg/l5 |  |
| Monochlorobenzene | 108907 | 0.1 mg/l |  |
| Styrene | 100425 | 0.1 mg/l |  |
| Tetrachloroethylene | 127184 | 0.005 mg/l |  |
| Toluene | 108883 | 1 mg/l |  |
| Trichloroethylene | 79016 | 0.005 mg/l |  |
| 1,1,1-Trichloroethane | 71556 | 0.2 mg/l |  |
| 1,2,4-Trichlorobenzene | 120821 | 0.07 mg/l |  |
| 1,1,2-Trichloroethane | 79005 | 0.005 mg/l |  |
| Vinyl Chloride | 75014 | 0.002 mg/l |  |
| Xylenes (total) * Chemical Abstract Service Registry Number | 1330207 | 10 mg/l |  |

Synthetic Organic Compounds

| Parameter | CASRN | # MCL | Monitoring Requirements |
| --- | --- | --- | --- |
| Alachlor | 15972608 | 0.002 mg/l | Monitoring frequency depends on MassDEP–approved sampling plan. Community and non-transient non-community water supply sources must initially monitor for four consecutive quarters. Non-vulnerable sources may be granted monitoring waivers. 6Statewide waivers have been approved by the U.S. EPA for both ground and surface waters. 7Statewide waivers have been approved by the U.S. EPA for surface waters. |
| Atrazine | 1912249 | 0.003 mg/l |  |
| Benzo(a)pyrene | 50328 | 0.0002 mg/l |  |
| Carbofuran | 1563662 | 0.04 mg/l |  |
| Chlordane | 57749 | 0.002 mg/l |  |
| Dalapon | 75990 | 0.2 mg/l |  |
| Di(2-ethylhexyl) adipate | 103231 | 0.4 mg/l |  |
| Di(2-ethylhexyl) phthalate | 117817 | 0.006 mg/l |  |
| Dinoseb | 88857 | 0.007 mg/l |  |
| Diquat6 | 85007 | 0.02 mg/l |  |
| 1,2-Dibromo-3-chloropropane (DBCP)7 | 96128 | 0.0002 mg/l |  |
| 2,4-D (2,4-Dichlorophenoxyacetic acid) | 94757 | 0.07 mg/l |  |
| Endothall5 | 145733 | 0.1 mg/l |  |
| Endrin | 72208 | 0.002 mg/l |  |
| Ethylene dibromide (EDB) | 106934 | 0.00002 mg/l |  |
| Glyphosate6 | 1071536 | 0.7 mg/l |  |
| Heptachlor | 76448 | 0.0004 mg/l |  |
| Heptachlor epoxide | 1024573 | 0.0002 mg/l |  |
| Hexachlorobenzene | 118741 | 0.001 mg/l |  |
| Hexachlorocyclopentadiene | 77474 | 0.05 mg/l |  |
| Lindane | 58899 | 0.0002 mg/l |  |
| Methoxychlor | 72435 | 0.04 mg/l |  |
| Oxamyl (Vydate) | 2313522 | 0.2 mg/l |  |
| Polychlorinated biphenyls (PCBs) | 1336363 | 0.0005 mg/l |  |
| Pentachlorophenol | 87865 | 0.001 mg/l |  |
| Picloram | 1918021 | 0.5 mg/l |  |
| Simazine | 122349 | 0.004 mg/l |  |
| 2,3,7,8-TCDD (Dioxin)6 | 1746016 | 3x10-8 mg/l |  |
| Toxaphene | 8001352 | 0.003 mg/l |  |
| 2,4,5-TP (Silvex) | 93721 | 0.05 mg/l |  |

Turbidity

| Parameter | # MCL | Monitoring Requirements |
| --- | --- | --- |
| Turbidity | 1 NTU (Nephelolometric turbidity unit) | Applies to Community and Non-community systems using filtered or unfiltered surface water sources. Monitoring is required daily. Non-community systems may reduce sampling if granted MassDEP approval to do so. |

Disinfectants/Disinfection Byproducts

| Parameter | CASRN | # MCL | Monitoring Requirements |
| --- | --- | --- | --- |

| Chlorine (as Cl2) | 7782505 | 4.0 mg/l | Monitoring frequency depends on MassDEP–approved sampling plan and type of treatment being used. Applies to Community and non-transient non-community systems which add a chemical disinfectant (oxidant) to the water. 8Also applies to Transient non-community (TNC) systems. |
| --- | --- | --- | --- |
| Chloramines (as Cl2) | -- | 4.0 mg/l |  |
| Chlorine dioxide (as ClO2)8 | 10049044 | 0.8 mg/l |  |
| Total Trihalomethanes: chloroform bromodichloromethane dibromochloromethane bromoform | 67663 75274 124481 75252 | 0.080 mg/l |  |
| Haloacetic Acids (five): monochloroacetic acid dichloroacetic acid trichloroacetic acid monobromoacetic acid dibromoacetic acid | 79118 79436 76039 79083 631641 | 0.060 mg/l |  |
| Bromate | 15541454 | 0.010 mg/l |  |
| Chlorite | 7758192 | 1.0 mg/l |  |

Bacteria

| Parameter and MCL | Monitoring Requirements |
| --- | --- |
| ## Coliform Bacteria A) MCL- More than one total coliform-positive sample if collecting 40 or fewer samples per month, or more than 5% positive if collecting more than 40 samples per month. B) Acute MCL - Any E.coli-positive or fecal coliform-positive repeat sample, or any total coliform-positive repeat sample following an E.coli-positive routine sample. | Applies to all systems. The number of samples collected depends on the population served (see 310 CMR 22.05, Table 1-22.05). The range is from 1/month for systems serving  1,000 persons to 480/month for systems serving > 3,960,000. Non-community systems must sample no less than quarterly. |
| Ground Water Rule (GWR) Fecal indicators – E coli, enterococci, and coliphage (See 310CMR 22.26(3)(a)3 to determine the applicable fecal indicator for your system) MCL - Any fecal indicator positive sample in a ground water source that does not have MassDEP certified 4-log treatment. | Applies to all systems with ground water sources that do not have MassDEP certified 4-log treatment. Monitoring is triggered if the source has a confirmed positive Total Coliform Rule (TCR) distribution sample. One (1) raw water sample is required for each of the ground water sources in use at the time of the TCR positive result. Representative sampling may be allowed with prior MassDEP approval. If the initial sample (s) is positive 5 additional samples are required. |

Radionuclides

| Parameter | CASRN | MCL | Monitoring Requirements |
| --- | --- | --- | --- |
| Gross Alpha Particle Activity9 | -- | 15 pCi/l | Community systems must monitor for 4 consecutive quarters prior to December 31, 2007. Grandfathering of historic data or no detections during the first two quarters may reduce this requirement. Future monitoring requirements are based on the results of this initial period. 9Includes radium-226 but excludes radon and uranium. 10If the gross alpha particle activity is  5 pCi/l, it may be substituted for the required radium-226 analysis. If the gross alpha particle activity is  15 pCi/l, it may be substituted for the required uranium analysis. 11Monitoring is required only at those systems designated by MassDEP. |
| Combined Radium-22610 and Radium-228 | 7440144 | 5 pCi/l |  |
| Uranium10 | 7440611 | 30 ug/l |  |
| Beta Particle Activity11 | -- | 4 mrem/yr |  |
| Photon Radioactivity11 | -- | 4 mrem/yr |  |
| Average Annual Concentrations which produces a body or organ dose of 4 mrem/yr |  |  |  |
| Tritium | 10028178 | 20,000 pCi/l |  |
| Strontium-90 | 10098972 | 8 pCi/l |  |

Massachusetts Drinking Water Guidelines

This list of public water supply guidelines are for chemicals that do not have MCLs/MRDLs. MassDEP’s Office of Research and Standards (ORS) derives these guidelines, and adopts or revises U.S. EPA health advisories and proposed MCLs. New guidelines are evaluated on a case-by-case, ongoing basis and may be incorporated into the list at any time.

For information on the derivation of the guidelines, and for general information on the health effects of water contaminants, please contact ORS at 617-292-5570 or visit http://www.mass.gov/dep/toxics/chemical.htm .

| Parameter |  | CASRN | Guideline (mg/l) | Monitoring Requirements |
| --- | --- | --- | --- | --- |
| Acetone |  | 67641 | 6.3 | On a case by case basis MassDEP may require systems to monitor for one or more of the chemicals. 12Non-chlorinated supplies only. 13The overlap in the C9-C12 range is the result of the VPH and EPH analytical methods used to quantitate these ranges of petroleum hydrocarbons in drinking water. The choice of the most appropriate range to use is based on the identity of the petroleum product of concern and is therefore determined on a case-specific basis. 14EPA has proposed an MCL of 300 pCi/l. 15The sodium guideline is based on an 8-ounce serving. |
| Aldicarb |  | 116063 | 0.003 |  |
| Aldicarb sulfone |  | 1646884 | 0.002 |  |
| Aldicarb sulfoxide |  | 1646873 | 0.004 |  |
| Bromomethane |  | 74839 | 0.01 |  |
| Chloroform12 |  | 67663 | 0.07 |  |
| Dichlorodifluoromethane |  | 75718 | 1.4 |  |
| 1,1-Dichloroethane |  | 75343 | 0.07 |  |
| 1,3-Dichloropropene |  | 542756 | 0.0004 |  |
| 1,4-Dioxane |  | 123911 | 0.003 |  |
| Ethylene glycol |  | 107211 | 14 |  |
| Methyl ethyl ketone |  | 78933 | 0.35 |  |
| Methyl isobutyl ketone |  | 108101 | 4.0 |  |
| Methyl tertiary-Butyl Ether |  | 1634044 | 0.07 |  |
| Metolachlor |  | 51218452 | 0.1 |  |
| Naphthalene |  | 91203 | 0.140 |  |
| Nickel |  | 7440020 | 0.1 |  |
| Petroleum Hydrocarbons |  |  |  |  |
| TPH (Total petroleum hydrocarbons) |  | N/A | 0.2 |  |
| Aliphatics | C5-C8 | 30080 | 0.3 |  |
|  | C9-C1213 | 30089 | 0.7 |  |
|  | C9-C1813 | 30092 | 0.7 |  |
|  | C19-C36 | 30057 | 14.0 |  |
| Aromatics | C9-C10 | 30087 | 0.2 |  |
|  | C11-C22 | 30048 | 0.2 |  |
| Radon-22214 |  | 14859677 | 10,000 pCi/l |  |
| Sodium15 |  | 7440235 | 20 |  |
| Tetrahydrofuran |  | 109999 | 1.3 |  |
| 1,1,2-Trichloro-1,2,2-Trifluoroethane (Freon 113) |  | 76131 | 210 |  |
| Tertiary Amyl Methyl Ether (TAME) |  | 994058 | 0.09 |  |
| Tertiary Butyl Alcohol (TBA) |  | 75650 | 0.12 |  |

Massachusetts Secondary Standards

Massachusetts has secondary standards for drinking water. The parameters listed below are not known to cause a health risk at or below the secondary standard, but may affect the taste, color, and/or odor of drinking water.

| Parameter | CASRN | Secondary MCL (mg/l) | Monitoring Requirements |
| --- | --- | --- | --- |
| Aluminum | 7429905 | 0.05 to 0.2 | Secondary standards are used to determine aesthetic quality and enhance water operations as such MassDEP strongly recommends that systems annually monitor for all secondary standards. On a case by case basis MassDEP may require systems to monitor for secondary standards. 16Based on EPA’s Drinking Water Advisory using taste and odor thresholds. 17EPA has proposed an MCL of 500 mg/l. |
| Chloride | 7647145 | 250 |  |
| Color | N/A | 15 color units |  |
| Copper | 7440508 | 1 |  |
| Corrosivity | N/A | Non-corrosive |  |
| Fluoride | 7782414 | 2 |  |
| Foaming agents | N/A | 0.5 |  |
| Iron | 7439896 | 0.3 |  |
| Manganese | 7439965 | 0.05 |  |
| Methyl tertiary-Butyl Ether16 | 1634044 | 0.020 – 0.040 |  |
| Odor | N/A | 3 threshold odor numbers |  |
| pH | N/A | 6.5 to 8.5 |  |
| Silver | 7440224 | 0.10 |  |
| Sulfate17 | 7757826 | 250 |  |
| Total dissolved solids (TDS) | N/A | 500 |  |
| Zinc | 7440666 | 5 |  |