## Sheet1
Note: This spreadsheet is intended as an update to the MA TSRG and recommendations from the subgroup are subject to change. Items in green have been agreed upon by the subgroup.
IEEE 1547-2018 Topic | Section Number | Overview/Update to MA TSRG | Utility Consensus/Language for Interconnection Standards (if applicable) | Recommended Tariff Updates Required (if any)
Reference Point of Applicability | 1.4 | Accepted in concept. Utilities may need to clarify the requirements by making clear statements about particular DERs & sizes in accordance with tariff/utility requirements. | Utilities move to accept with potential additions/clarifications in utility interconnection requirements. Developers may need to provide supplemental equipment to detect abnormal voltages, etc according to 6.2 & 6.4 in the standard. Utility requirements should aim to make the requirements according to each size/configuration as clear as possible within existing requirements structure. | N/A
Enter Service: - Healthy Grid Parameters - Delay before enter service - Ramp rates in enter service | 4.10 | Accepted as-written. Recommend 10BD tariff milestone addition for processessing any "Exception 2" applications to utility/ISO. | "The DER shall not connect or return to service following a trip (including any ground fault current sources) until detecting 5 minutes of healthy utility voltage and frequency in accordance with IEEE 1547-2018 clause 4.10. The DER shall enter service in accordance with IEEE 1547-2018 Clause 4.10.3, part c). The DER active power output shall increase linearly or in a stepwise linear ramp with a default time of 300s, with steps no greater than 20% of the DER rating. The DER may increase slower than specified, or by other means requested by the DER impact study in accordance with 1547-2018. Exception 1 is permitted for all small-scale DERs in accordance with IEEE 1547-2018. Exception 2 will be evaluated on a case-by-case basis. DERs 500kVA and larger desiring to use Exception 2 shall send the rationale and request to the utility. An additional 10 BD will be required to be added to all tariff milestones to accommodate utility processing/review as well as ISO review. All requests are subject to utility and ISO acceptance. " | No changes to tariff, except: Enter Service Exception 2 will be evaluated on a case-by-case basis. DERs 500kVA and larger desiring to use Exception 2 shall send the rationale and request to the utility. An additional 10 BD will be required to be added to all tariff milestones to accommodate utility processing/review as well as ISO review. All requests are subject to utility and ISO acceptance.
Power Quality: DC Injection | 7.1 | Accept as written. | Adopt as written. | No tariff changes
Power Quality: Rapid Voltage Changes | 7.2.2 | Accept thresholds. *There are subgroup concerns with 3% vs. 5% at secondary voltages. Screens outside of subgroup scope / per utility interconnection requirements. MA is discussing screens in tariff, and it's expected that the screens working group will help with this. | Open for now: The interconnection of the DER facility shall not affect the utility nominal RMS voltage delivery at any distribution level PCC by greater than 3%, and shall not exceed the rapid voltage change limits required by IEEE 1547. Subgroup is also uncomfortable with shared secondary concern and threshold at 5% rather than 3% also. | Couple with tariff screens work
Power Quality: Flicker | 7.2.3 | Adopt the section as-is. The thresholds are acceptable. Note that IEEE 1453 and the IEC standard are recommended practice and outside the subgroup scope. | Adopt as written. | No tariff changes.
Power Quality: Limitation of Current Distortion (Harmonics) | 7.3 | Adopt section as-is, with additional requirement for higher-order harmonics. | The DER shall not cause harmonic current distortion in violation of the limits given in IEEE 1547. The utility reserves the right to require the DER owner to mitigate All order harmonics not otherwise limited by IEEE 1547 to no higher than 0.3% if they affect other PCCs. | Tariff section needs update (refers to 2003). Update to 'most current version' (or to 2018 document if members see issue with 'most current version.'
Power Quality: Limitation of overvoltage over one fundamental frequency period | 7.4.1 | Adopt section with PCC margin notice. | The DER shall not cause line to line or line to ground overvoltages on the Area EPS in violation of IEEE 1547-2018. Where DERs are required to be effectively grounded, utilities recommend to design for no higher than 125% LG overvoltages at the PCC in accordance with utility requirements to avoid violating the standard elsewhere on the feeder. | No tariff updates expected.
Power Quality: Limitation of cumulative instantaneous overvoltage | 7.4.2 | Adopt section as-is. | Adopt as written. | No tariff update expected.
Present Topics Being Discussed: - Draft recommendations for the following are expected to be finalized early December: * Abnormal Conditions Categories (I, III, III) * Frequency Droop Settings * Voltage Trip Setings * Frequency Trip Settings - Voltage regulation discussion will begin Oct 7th - Glide Path / Hurdles to full implementation / Phase II, III adoption milestones & needs - A brief on communications is expected Nov 4th