## MTSRG Matrix
|  | National Grid | Eversouce MA (East) | Unitil | Eversource MA (West)
ID | Topic
1 | Anti-islanding | Sandia screening method. If a screen is failed, a detailed islanding study is conducted. | No official anti-islanding position | Load:Generation screening per feeder section. If a screen is failed, a detailed islanding study is conducted. | Load:Gen screening per feeder section, during SIS. If a screen is failed, DTT is required (no detailed islanding study).
| PV | (DG > 67% of load) + (reactive power match within 1%) |  | (DG > 50% of load) | (DG > 33% of load)
| PV parallel with wind | (Wind > 20% of PV) |  | N/A | (DG > 33% of load)
| Rotating generation | (DG > 33% of load) |  | (DG > 33% of load) | (DG > 33% of load)
2 | Direct Transfer Tripping | DTT is required for anti-islanding protection only. | DTT is considered for projects over 1 MW. Triggered by reverse power flow (unless xfmr manufacturer provides a letter notifying NSTAR of reverse power flow capability), flicker, high voltage, or other issues discovered in SIS. | DTT is required for anti-islanding protection, or fault mitigation at transmission level | DTT is required for anti-islanding protection, or in the event of loop-scheme transfers
| Primary medium | Telecom Line | Telecom Line | Telecom Line | Telecom Line
| Alternatives | Radio, 900MHz, line-of-sight restrictions | Radio, 900MHz, line-of-sight restrictions | Power Line Carrier | Radio, 900MHz, line-of-sight restrictions
|  | Pulse-based PLC, single transmitter at substation, receiver at each DG | PDR2000, high-speed tripping | Pilot Program: Cellular-based | Power Line Carrier
Fiber with passive signal
3 | Feeder Capacity Limits | No hard Limit. Capacity issues are considered on a project-by-project basis. | No hard limit. LTC operations are studied in SIS. Active VAR compensation will not be permitted on distribution feeders. | No hard limit. Capacity issues are considered on a project-by-project basis. | No hard limit. Capacity issues are considered on a project-by-project basis. Projects with load:generation mismatch are red-flagged in application process.
| Minimum load factor | min = (.25)*(peak) | min = (.25)*(peak) | min = (.25)*(peak) | min = (.25)*(peak)
| Alternative capacity studies | Long-Term Dynamic Modelling used by subs (Cym) | No dynamic modeling | No dynamic modeling | No dynamic modeling
4 | Remote Control & Monitoring | IPP's: Pole-top recloser utilized for analog and status points at POI. Non-IPP (true net meter): RTU required at DG > 500kW for 5kV circuits, DG > 1MW for 15kV circuits, DG > 1.8 MW for +15kV circuits | PCC reclosers are SCADA capable. Safety trip (high-speed) for induction machines to prevent closing in an unsynched gen. Non-safety trip (radio) used to mitigate flicker, high voltage, etc. Monitors net power at PCC. | PCC reclosers are SCADA capable. Monitors: kVA, kW, kVAr. Not implemented for remote generator disconnect | PCC reclosers are SCADA capable. Monitors: unkown. Reclosers can be remotely opened by dispatch.
| Medium |  | MDS Radio | N/A | N/A
| Alternatives |  | PDR2000, fiber | Any device capable of DNP3 on generator disconnect.
5 | Threshold DG size, PCC Recloser | DG > 1000kW @ 15kV, DG > 500kW @ 5kV | DG > 1MW | DG > 1MW | DG > 1MW
6 | External disconnects, small generation | Requirements outline in ESB 756 C | Projects in Simplified Track do not require external disconnect. Discussing 10-25kW range internally.
| Threshold DG size | DG < 25kW | DG < 10-25kW | DG < 10kW | DG <10kW
7 | Witness Test Requirements | DG > 500kW, witness test required for customer redundant relay. DG < 500kW, internal relaying & UL certification is satisfactory. Approved 3rd party conducts test, Ngrid representative attends for supervision and approval of results. ESB 756 C provides a sample witness test procedure. | DG < 200kW, customer submits pictures of installation, documentation of UL listing of equipment, compliance with applicable codes. DG > 200kW requires witness test. Customer redundant relay testing for: PV > 1MW, synchornous gen > 500kW, and all asynchronous gen. | Simplified Track, witness test while meter is being replaced with bidirection unit. | DG < 30kW, witness test confirms that the system is installed per application, 2 sec trip, and 5 minute reconnection window. For DG > 30kW witness test of customer redundant relay.
| Required documentation | Witness test procedure, outlining test equipment, set-points under test, energization plan. | Stamped 14-point checklist, one-line, three-line, relay elementary, logic and tripping diagram, coordination study & relay settings for approval. | Witness test procedure, outlining test equipment, set-points under test. | Certified test results for customer relay, print-out of inverter settings, one-line, three-line, relay schematic. Review by NU P&C group prior to witness test.
| Required test points | 27, 59, 81o/u, 51N, 51C, 59N in accordance with IEEE 1547. Underfrequency ridethrough to be modified according to NPCC A.03 curve. Clearing times include breaker operation. | 27, 59, 81o/u, 51N, 51, 59N in accordance with IEEE 1547. Underfrequency ridethrough to be modified according to NPCC A.03 curve. Clearing times include breaker operation. | 27, 59, 81o/u, 51N, 51, 59N in accordance with IEEE 1547. Clearing times include breaker operation. | 27, 59, 81o, 51N, 51C, 59N in accordance with IEEE 1547. Underfrequency ridethrough to be modified according to NPCC A.03 curve at 57Hz.
| Failure protocol | 10% error window for setpoints. Technician to troubleshoot and retest failed elements. | Reschedule and retest failed elements. | Reschedule and retest failed elements. | Reschedule and retest failed elements.
9/16/13 Session
8 | Xfmr Winding Configurations | Wye-G x delta (fully isolated neutral, Wye-g x wye-g with effectively grounded source, Wye-g x wye-g with secondary grounding bank, Delta x wye-g with primary grounding bank | Delta x wye, Wye-g x Delta, Wye-g x wye-g | Wye-g x delta | Application by application
| Notes | Grounding source required for DG > 500kW | 59N required for Delta x wye |  | System must be effectively grounded at PCC
| Grounding Reactors | NGR required if ground fault detection is compromised | NGR required based on X/R ratio | NGR required if ground fault detection is compromised
| Ungrounded feeders | Handful of ungrounded circuits in service territory | Ungrounded circuits in service territory | No ungrounded circuits | Handful of ungrounded circuits in service territory
9 | Customer redundant relaying | DG > 500kW | DG > 1MW | No threshold | DG > 500kW
| Notes | See Witness test notes for required setpoints | See Witness test notes for required setpoints | See Witness test notes for required setpoints | See Witness test notes for required setpoints
| Location | Upstream of grounding source, depends on xfmr config | Upstream of grounding source, depends on xfmr config | Upstream of grounding source, depends on xfmr config | Upstream of grounding source, depends on xfmr config
| Remote operators permitted | Yes | Yes | Yes | Yes
10 | Reverse Power Flow | Permitted | Permitted | Conditionally permitted | Permitted
| Notes | 59N required on supply xfmr high sides if: | Beckwith M-2001D and M-0239B LTC controller required | DTT may be required to mitigate transmission faults at stations with no high side VT's | Beckwith M-2001D and M-0239B LTC controller required
|  | Aggregate DG > (.66)*(min load @ N-1) | RPF capacity can be limited to between 75%-100% of transformer nameplate on case-by-case basis | 59N required on supply xfmr high | RPF capacity can be limited to between 75%-100% of transformer nameplate on case-by-case basis
Where N-1 stipulates that the most heavily loaded feeder is removed from the calculation
Transmission < 115kV, VT's required
Transmission > 115kV, CCVT's required
11 | Minimum Load, Simplified on Networks | DG < (1/15)*(min load of customer) | DG < (1/15)*(min load of customer) | DG < (1/15)*(min load of customer) | DG < (1/15)*(min load of customer)
12 | Power Factor Requirements | +/- .95 | 1.0 | +/- .95 | +/- .95
| Notes | DG may provide static pf regulation at PCC | Unity required at generator terminals | IPP: PF measured at DG terminals | Impact studies are performed at unity
|  | If the circuit has no voltage regulators, the DG may provide active pf regulation |  | Non-IPP: PF measured at PCC
Active pf regulation is not permitted