## Sheet1
PSCAD Checklist | Notes | Comments from Manufacturer/Developer
According to the one-line-diagram, is this the correct inverter model, manufacturer, and version? | Developers to confirm with manufacturer.
Does the PSCAD inverter model contain all necessary libraries? | Typically, libraries have *.lib or *.obj file extensions. The PSCAD model submission should also include any required files, including but not limited to *.dll files and .txt files.
Is the PSCAD model compatible with the passive equipment between the point of interconnection (POI) and the point of common coupling PCC, including the GSU, grounding equipment, inverters or controller shown in the one-line diagram? | Ensure that the inverter model is compatible with GSU and its configuration, grounding transformer, neutral grounding reactance, capacitor banks, and surge arresters. For passive elements, the developers should provide information either in the form of a single-line drawing or an Excel spreadsheet.
Is there a user manual with instructions included with the PSCAD model package? | Ensure that the manuals are submitted along with the inverter models. A typical manual would include at a minimum the sections for "How to Run the PSCAD Model", Descriptions of Modules and Elements of the inverter model", "Description of Protection Device Settings", "SPOV Enablement", and "Modes of Inverter Operations/Functions".
Does the model have a Self-Protection Over-Voltage (SPOV) function? What is the default SPOV setpoint? • What is the range of SPOV setpoints available for the inverter? • Does the model package have instructions on how to enable and disable the SPOV setpoints? • Does the model package have instructions on how to change the SPOV setpoints for mitigation purposes? | These mechanisms, referred to as SPOV mechanisms cause the inverter to cease to energize when the circuit voltage exceeds certain limits. The SPOV mechanisms thus can prevent both ground fault overvoltage (GFOV), and load-rejection overvoltage (LROV). Normally the voltage range is between 1.2 to 1.4 pu while the time threshold that the inverter can tolerate is about a few miliseconds. The Manufacturer should issue a letter confirming the inverter model has user adjustable SPOV settings with required threshold time to trip? The SPOV setting should be adjustable in the PSCAD model.
Does the model implement the required ISO_NE OV/UV/OF/UF settings or can those be set manually? (if user-configurable, then the manual should instruct how to modify those settings) | Developers to confirm with manufacturer. Either these settings can be hardcoded, or user-configurable, as long as the settings can be set to the ISO-NE requirement.
Does the model work at 60 Hz? | Developers to confirm with manufacturer.
Does the model have anti-islanding module implemented for Risk of Islanding testing? Does the model turn off according to the latest IEEE 1547 standard after modeling a loss of source? (The current requirement is within 2 seconds) | Manufacturer to provide the letter for their approach of anti-islanding detection (and their method), and if the model equipped with island detection module.
Does the PSCAD inverter model have the following options? 1. Does the model have a way to scale output? 2. Does the model have the reactive power functions required by latest IEEE 1547 standard, including constant power factor mode, constant reactive power mode, frequency-active power mode, voltage-reactive power mode, and active power-reactive power modes? 3. Does the inverter model have the capability to change the real/reactive power set/reference? | Scaling output module (either as a separte module or as a scaling transformer) is used to scale the output of the inverter. Please note that Point 2 is related to the mode of the inverter, but Point 3 is related to change the Pref and Qref of the inverter model. This is quite different than scaling output which scales the real P and Q output of the system. Manufacturer should address the questions in the provided user's Manual.
Does the model include rate of change of frequency (RoCoF) and phase jump protection settings as tested in latest UL1741 certificate? | Manufacturer to provide the UL1741SA/ UL1741SB Edition 3 (or latest) certificate, which is considered sufficient as per Sections 1.6 and 1.7 of “Default IEEE 1547-2018 Setting Requirements” Document.
The PSCAD Checklist should be completed and submitted along with package submission.