INDOOR AIR QUALITY ASSESSMENT

Goodell Hall
University of Massachusetts
140 Hicks Way
Amherst, Massachusetts

[image: image20.png]= Stay bome from wock and school if you get sck with » flu-like illness

ul avedd centact with sthers
¢ does not spread. Stay at home until you have been free from fever for at least 24 hours
after your last dose of fever- reducing medication (like Tylenol, Advil or Motrin). For most people
this will mean staying at home for abovt four days.

How do | take care of someone Who s sick with H1N1 flu?
Flu: What You Can Do - Caring for People At Home s a booklet availsble in nine lngunges
lotsof information to belp yor eare for someane who has the f in heir hon

 gives you
A video isalso available in
i

English and Spanish. Flu: What Tou Can Do information can be fourd at: mass.

Where can I get more information?
fass 2-1-1 provides fl information forthe general public:csll 211 or 1-577-21 1-MASS (6277,
Tnterpreter services available in many langusges.

« Call your dostor, murse or clini, or your loesl board of helth

« Call the MA Department of Public Health, Tnumunization Program ar: (617) 983-6500 or toll-free t
6582850

« Massachuserts Depariment of Public Health website af mass.ov fin
« Cenerfor Disease Cantrol and Prevention (CDC) at: wwww eds zar/fly

For flu clinie iaformation, visit the MassPRO Publie Flu Clinie Finder website at:ho:/flu masspro.ore.





Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health Assessment

February 2010

Background/Introduction

In response to a request from Dr. Maureen O'Leary, Assistant Director, Academic Safety & Environmental Health Program, University of Massachusetts (UMASS), an indoor air quality assessment was conducted at Goodell Hall, 140 Hicks Way, Amherst, Massachusetts.  The Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health Assessment (BEH) conducted the assessment.  BEH staff received complaints of general indoor air quality problems as well as health concerns that occupants attributed to the building.  On October 9, 2009, a visit to conduct an assessment of Goodell Hall was made by Michael Feeney, Director of BEH’s Indoor Air Quality (IAQ) Program.  Mr. Feeney was accompanied by Lisa Hébert and James Tobin, Environmental Analysts/Indoor Air Inspectors in BEH’s IAQ Program. 
Goodell Hall was constructed in 1935 as a library and was converted into office space for the UMASS graduate admissions program.  The original building is a three-story structure with a basement, which is now occupied.  A four-story wing was added to the rear of the original building in the post World War II era.  The addition included a rooftop penthouse that houses the entire building’s heating, ventilating and air-conditioning (HVAC) system.  Windows are openable in some areas of the building. 
Methods

Air tests for carbon dioxide, temperature and relative humidity were taken with the TSI, Q-Trak, IAQ Monitor, Model 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  BEH staff also performed visual inspection of building materials for water damage and/or microbial growth.  
Results

The offices at Goodell Hall have an employee population of approximately 405.  Tests were taken under normal operating conditions and results appear in Table 1.  

Discussion

Ventilation

It can be seen from Table 1 that the carbon dioxide levels were below 800 ppm in all but 1 of 83 areas surveyed (Table 1), indicating adequate ventilation exists in the majority of the building.  The HVAC system consists of a series of large air-handling units (AHUs) located in the rooftop penthouse (Picture 1).  Each AHU is connected to ceiling-mounted fresh air diffusers via ductwork.  Air is returned to the AHUs by ceiling-mounted vents connected to ductwork.  The original building has a set of AHUs in closets, which are connected to occupied space via ductwork (Picture 2).  The HVAC system was operating during the assessment.  Walls erected during the remodeling to create additional office space separated some supply vents from their corresponding return vents.  As a result, some occupied areas do not have complete fresh air supply and return ventilation capacity.  Occupied spaces need sufficient fresh air supply and return in order to create airflow.  Ordinary indoor air pollutants can build up in an area if HVAC system components are missing.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The date of the last balancing of these systems was not available at the time of the assessment.  

The Massachusetts Building Code requires that each room have a minimum ventilation rate of 20 cubic feet per minute (cfm) per occupant of fresh outside air or openable windows (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, please see Appendix A.

Temperature readings recorded during the assessment ranged from 69 (F to 79 (F, which were within the MDPH’s recommended comfort range in most areas (Table 1).  The MDPH recommends that indoor air temperatures be maintained in a range of 70 (F to 78 (F in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.  

Relative humidity measurements ranged from 41 to 53 percent, which were within the BEH comfort guidelines in all areas surveyed.  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels would be expected to drop during the winter months due to heating and decreased outdoor relative humidity concentrations.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.
Microbial/Moisture Concerns

The lowest level of the building is used for record storage.  This area has been subdivided using cyclone fencing, which allows for free air movement.  A large number of paper records are stored in this area in filing cabinets constructed of heavy cardboard (Picture 3).  A distinct, pungent odor of moistened cardboard was detected in this space.  Located in this area are a fresh air supply and return vent that are likely connected to the general HVAC system (Picture 4).  Odors from the stored materials in the lower level can be captured by the HVAC system and distributed into other areas of the building.
The likely source of moisture in this area is the building’s mechanical room, which is located below the records storage room.  The building does not contain a furnace.  Steam is pumped into this mechanical room via piping from the UMass steam plant.  The mechanical room has a number of sources for leaking water and/or steam, including a significant number of pipe breaches (Picture 5) and a sump pump cistern (Picture 6).  Of note is the existence of a fan system (EB8) that appears to be an exhaust ventilation system dedicated to removing water vapor and air from the mechanical room.  At the time of the IAQ assessment, this fan was found deactivated, likely due to its location with its electric exhaust vent motor in a pool of standing water (Picture 7).  Without mechanical exhaust ventilation, water vapor can migrate from the mechanical room to the records storage room above.

Several conditions observed in the building indicate that water vapor and pollutants are migrating from the records storage area to occupied areas.  Air may be drawn up the elevator shafts to upper floors.  In addition, the building contains a number of abandoned dumbwaiters (Picture 8), which can allow for basement air to migrate to occupied spaces on upper floors.  The following concepts concerning heated air and elevators/dumbwaiters should be understood in order to explain how basement air may be impacting the upper floors:
1. Heated air will create upward air movement (called the stack effect).

2. Cold air moves to hot air, which creates drafts.

3. Airflow is created, intended or otherwise, from items that produce heat (e.g., fluorescent light bulbs).

4. As heated air rises, negative pressure is created, drawing cold air back to equipment creating heat.

5. Airflow created by the stack effect, drafts or mechanical ventilation can draw particulate matter into the air stream.

Each of these concepts has influence on the movement of basement pollutants to the upper floors.  As heated air rises in the stairwells, dumbwaiter and elevator shafts, basement air can enter each of these vertical shafts.  In addition to the stack effect, elevators can draw pollutants into the elevator shaft while cars operate.  This piston effect can serve to place the basement elevator lobby under negative pressure as the car moves upwards, enhancing the penetration of basement pollutants into occupied areas and hallways through doorframes and other holes in walls and ceilings.  

Water-damaged cardboard was also observed in the air-handling room.  Water-damaged paper products can serve as a source of mold growth and should be removed and discarded to prevent a source of respiratory irritation.

Water-damaged ceiling tiles were observed throughout the building (Picture 9).  In some areas, water damage to ceilings and walls has caused large areas to exhibit peeling paint.  Water-damaged walls and ceilings are an indication of leakage in the building, most likely from the roof.  The roof should be examined and repaired/replaced to prevent additional leaks and damage to the building.  Water-damaged materials should be repaired or replaced.
Water coolers were observed located over carpeted areas (Picture 10).  Overflow of the water basins or spills that often occur can moisten carpeting, which can lead to mold growth.  It is important that the catch basin of a water cooler be cleaned regularly as stagnant water can be a source of odors, and materials (i.e., dust) collected in the water can provide a medium for mold growth. 

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommends that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If porous materials are not dried within this time frame, mold growth may occur.  Water-damaged porous materials cannot be adequately cleaned to remove mold growth.  The application of a mildewcide to moldy porous materials is not recommended.   

Several areas contained a number of plants, many of which were located on carpeting (Picture 11).  Plant soil, standing water and drip pans can be a potential source of mold growth.  Drip pans should be inspected periodically for mold growth and over watering should be avoided.  Plants should also be located away from fresh air diffusers to prevent aerosolization of dirt, pollen or mold.

Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the school environment, BEH staff obtained measurements for carbon monoxide.  

Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health effects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  On the day of assessment, outdoor carbon monoxide concentrations were not detected (ND). (Table 1).  Carbon monoxide levels measured in the building were also ND.  

Particulate Matter (PM2.5)

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 microgram per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

Outdoor PM2.5 concentrations the day of the assessment was 17 μg/m3.  PM2.5 levels measured inside the building ranged from 5 to 10 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur in a building can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, cooking with the stoves and microwave ovens; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

TVOCs

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to identify materials that can potentially increase indoor VOC concentrations, BEH staff examined rooms for products containing these respiratory irritants.

Upon entering the dean’s office suite, the distinct odor of hand disinfectant was readily detected.  Hand disinfectant contains ethyl alcohol and fragrances, both of which can be an eye and respiratory irritant to some individuals (Betco Corporation, 2007; Birchwood Laboratories, Inc., 2007; B4 Brands by AMA, 2006; Georgia-Pacific Consumer Products, 2007).  According to MA DPH recommendations concerning H1N1 Flu, protection from flu virus can be achieved by either “[w]ash[ing] your hands often with soap and water or us[ing] alcohol based hand gel (MDPH, 2009, Appendix B).  
Some offices contained dry erase boards and dry erase markers.  Materials such as dry erase markers and dry erase board cleaners may contain volatile organic compounds (VOCs) (e.g., methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve), which can be irritating to the eyes, nose and throat (Sanford, 1999).

Air fresheners and deodorizing materials were observed in at least one area.  Air deodorizers contain chemicals that can be irritating to the eyes, nose and throat of sensitive individuals.  Many air fresheners contain 1,4-dichlorobenzene, a VOC which may cause reductions in lung function (NIH, 2006).  Furthermore, deodorizing agents do not remove materials causing odors, but rather mask odors that may be present in the area.  
Insect spray was observed in one office (Picture 12).  Pesticide use indoors can introduce chemicals into the indoor environment that can be sources of eye, nose and throat irritation.  The principles of integrated pest management (IPM) should be considered to remove pests in buildings.  
Other Concerns 
Several other conditions that can affect indoor air quality were noted during the assessment.  Numerous exhaust vents were obstructed throughout the building by bookcases, desks, computers, as well as by materials stored on shelving (Picture 13).  Occupants of the building have attempted to adjust the air flow within their space by obstructing the air diffusers in an effort to either reduce the volume of air or divert the direction of air as it enters the room (Picture 14).  Additional obstructions to airflow in the building are the numerous partitions that have been installed within the building.  These alterations can create an imbalance in the system, resulting in uneven heating/cooling conditions leading to occupant discomfort in other areas.  A few occupants expressed concerns to BEH staff regarding black particulate matter observed within their offices.  As airflow passes over the horizontal surfaces covering many air diffusers, dust which may have settled on the surface could easily become aerosolized within the occupied space.  Once aerosolized, the particulates will eventually settle on horizontal surfaces below.  
One cracked window in a women’s restroom was observed.  In addition to compromising the efficiency of the air-handling units in the building, this condition can allow unconditioned air into occupied space, potentially leading to condensation as well as mold growth.
Upholstered furniture was observed in some areas of the building.  Upholstered furniture is covered with fabric that comes in contact with human skin.  This type of contact can leave oils, perspiration, hair and skin cells behind.  Dust mites feed upon human skin cells and excrete waste products that contain allergens.  In addition, if relative humidity levels increase above 60 percent, dust mites tend to proliferate (US EPA, 1992).  In order to remove dust mites and other pollutants, frequent vacuuming of upholstered furniture is recommended (Berry, M.A., 1994).  It is also recommended that upholstered furniture (if present in schools), be professionally cleaned on an annual basis.  If an excessively dusty environment exists due to outdoor conditions impacting the indoor environment or indoor activities (e.g., renovations), cleaning frequency should be increased to every six months (IICRC, 2000).  Elevated outdoor levels of airborne particulates can result in increased levels of indoor particulates by entering into the building through open windows, doors and filter bypass. 

Several personal fans and return/exhaust vents had accumulated dust and debris.  Dust can be a source for eye and respiratory irritation.  If exhaust vents are not functioning, back drafting can occur and aerosolize dust particles.  When operating, they can serve to distribute settled dust particles.  Open ceiling plenums, missing ceiling tiles and open utility penetrations were observed.  These conditions have the potential to draw dusts, odors and vapors into occupied spaces.
An accumulation of paper was observed on the floor, bookcases and desks of some offices.  One office contained a large accumulation of stuffed toys.  Artificial plants were noted in some areas.  The large number of items stored in offices provides surfaces on which dust accumulates.  These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.  In addition, these materials can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

The HVAC system penthouse contained a large tub-like structure that was filled with debris (Picture 15).  This tub structure also contained a drain.  It is likely that the trap for this drain is dry, which could result in odors from the drain system to enter the HVAC mechanical room.  Drain system pollutants can be irritating to the eyes, nose and throat.
Conclusions/Recommendations

A decision should be made concerning the water-damaged and in some cases likely mold-contaminated materials stored in the basement.  If not addressed, these boxes, documents, books and other stored materials will continue to be a source of mold associated particulates.  Under current conditions, ventilation alone cannot serve to reduce or eliminate mold growth in these materials.  As an initial step, options concerning the preservation of materials stored in this area should be considered.  Since many of the materials appear to be of historical significance, an evaluation concerning disposition of them must be made.  Porous materials that are judged not worthy of preservation, restoration or transfer to another media (e.g., microfiche or computer scanning) should be discarded.  Where stored materials are to be preserved, restored or otherwise handled, an evaluation should be done by a professional book/records conservator.  This process can be rather expensive and should considered for conservation of irreplaceable documents that are colonized with mold.  Due to the cost of book conservation, disposal or replacement of moldy materials may be the most economically feasible option.  In view of the findings at the time of this visit, the following recommendations should be considered: 

1. Repair sources of leaking water and steam in the building’s mechanical room.  Eliminate sources of pooled water on the mechanical room floor.
2. Repair exhaust fan (EB8) located in the mechanical room to ensure that water vapor and air will once again be removed from the mechanical room.

3. Consider permanently sealing off dumbwaiters to eliminate pathways for movement of odors, particulate matter, etc to each floor.

4. Ensure leaks are repaired and replace water damaged ceiling tiles.  Examine the area above and around these areas for mold growth.  Disinfect areas of water leaks with an appropriate antimicrobial.

5. Place water coolers located in carpeted areas on surfaces that are impervious to water, such as a rubber mat.  Clean catch basins regularly.
6. Consider eliminating the practice of placing plants directly onto carpeted areas.  Examine drip pans periodically for mold growth.  Disinfect with an appropriate antimicrobial where necessary.  In addition, plants should be located away from the air stream of ventilation sources to prevent aerosolization of mold, pollen and particulate matter.

7. Clean dry erase marker trays to prevent the build-up of excessive particulates.  Consider purchasing low-odor emitting markers in order to decrease the concentration of VOCs in the classroom.
8. Encourage hand washing consistent with the MDPH to protect against H1N1 flu.  These include:
a. Get vaccinated when the vaccine becomes available, especially if you have a medical condition which makes health complications from the flu more likely.

b. Wash your hands often with soap and water or use alcohol based hand gel.

c. Cough or sneeze into a tissue or the inside of your elbow if you don’t have a tissue.  Throw the tissue in the trash and wash your hands.

d. Use a regular household cleaner to clean surfaces that might get flu virus on them like door knobs, phones, faucets and toys.

e. Stay home from work and school if you get sick with a flu-like illness and avoid contact with others so the virus does not spread.  Stay at home until you have been free from fever for at least 24 hours after your last dose of fever-reducing medication (like Tylenol, Advil or Motrin).  For most people this will mean staying at home for about four days (MDPH, 2009).

9. Consider discontinuing use of air deodorizers and insect sprays within the building.

10. Discontinue practice of obstructing ventilation components, both supply and exhaust vents.  Once the system is properly balanced, air flow within the occupied space should meet comfort parameters for the majority of occupants.  Consider having the systems balanced by an HVAC engineering firm every five years.  
11. Repair cracked window in women’s room.

12. Professionally clean upholstered furniture on an annual basis.

13. Clean personal fans, air diffusers, exhaust, return vents artificial plants periodically of accumulated dust.
14. Remove unnecessary papers, boxes, stuffed toys from offices in order to assist in keeping office in a clean condition.

15. For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

References

ACGIH. 1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment. American Conference of Governmental Industrial Hygienists, Cincinnati, OH.
ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 62-1989 

B4 Brands by AMA.  2006.  Avant OriginalTM Instant Hand Sanitizer Materials Safety Data Sheet.  B4 Brands by AMA., Nixa, MO. 

Berry, M.A.  1994.  Protecting the Built Environment: Cleaning for Health, Michael A. Berry, Chapel Hill, NC.
BETCO Corporation.  2007.  Clario Foaming Alcohol Instant Hand Sanitizer Material Safety Data Sheet.  BETCO Corporation, Toledo, OH.

Birchwood Laboratories, Inc.  2007.  Hand Wipe Take Alongs Materials Safety Data Sheet.  Birchwood Laboratories, Inc., Eden Prairie, MN.  

BOCA. 1993.  The BOCA National Mechanical Code/1993.  8th ed.  Building Officials & Code Administrators International, Inc., Country Club Hills, IL.
Georgia- Pacific Consumer Products.  2007.  Cormatic® High Capacity Instant Hand sanitizer Material Safety Data Sheet.  Georgia- Pacific Consumer Products, Atlanta, GA.
IICRC.  2000.  IICRC S001 Reference Guideline for Professional On-Location Cleaning of Textile Floor Covering Materials Institute of Inspection, Cleaning and Restoration Certification.  Institute of Inspection Cleaning and Restoration, Vancouver, WA.
MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

MDPH.  2009.  Public Health Fact Sheet H1N1 Flu (Swine Flu).  Massachusetts Department of Public Health, Boston, MA.  http://www.mass.gov/Eeohhs2/docs/dph/cdc/factsheets/swine_flu.pdf
NIH. 2006.  Chemical in Many Air Fresheners May Reduce Lung Function.  NIH News.  National Institute of Health .  July 27, 2006.  http://www.nih.gov/news/pr/jul2006/niehs-27.htm.
OSHA. 1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R. 1910.1000 Table Z-1-A.

Sanford.  1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo( Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.
SBBRS. 1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0 

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA.  1992.  Indoor Biological Pollutants.  US Environmental Protection Agency, Environmental Criteria and Assessment Office, Office of Health and Environmental Assessment, research Triangle Park, NC.  EPA 600/8-91/202 January 1992.

US EPA.  2001. Mold Remediation in Schools and Commercial Buildings.  US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, DC.  EPA 402-K-01-001.  March 2001.

US EPA.  2006. National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC. http://www.epa.gov/air/criteria.html. 

Picture 1

[image: image1.jpg]


[image: image2.jpg]



Rooftop Penthouse

Picture 2

[image: image3.jpg]



AHUs in Closets

Picture 3

[image: image4.jpg]



Records Stored In Basement

Picture 4

[image: image5.jpg]



Fresh Air Supply And Return Vent In Records Storage Area.

Picture 5

[image: image6.jpg]



Pipe Breach

Picture 6

[image: image7.jpg]



Sump Pump Pit Filled With Water

Picture 7

[image: image8.jpg]



EB8 Exhaust Vent Motor in Standing Water

Picture 8

[image: image9.jpg]



Abandoned Dumbwaiter Door on Upper Level of Building

Picture 9

[image: image10.jpg]



Water Damaged Ceiling Tiles

Picture 10

[image: image11.jpg]



Water Coolers over Carpeting

Picture 11

[image: image12.jpg]



Plants on Carpeting

Picture 12

[image: image13.jpg]



Insect Spray

Picture 13

[image: image14.jpg]



Blocked Air Vent

Picture 14

[image: image15.jpg]



Vent Covered With Cardboard.

Picture 15

[image: image16.jpg]



Tub-Like Structure in the HVAC Penthouse Filled With Debris

	Location
	Occupants

in Room 
	Temp

(°F) 
	Relative

Humidity

(%)
	Carbon

Dioxide

(ppm)
	Carbon Monoxide

(ppm)
	PM2.5

(µg/m3)
	Windows

Openable
	Ventilation
	Remarks

	
	
	
	
	
	
	
	
	Supply
	Exhaust
	

	Background:
	-
	69
	55
	510
	ND
	17
	-
	-
	-
	

	Admin. Office
	4
	70
	50
	572
	ND
	6
	Y
	Y*
	Y
	DO, Plants, Copier, * Blocked supply

	Advising
	2
	70
	50
	662
	ND
	6
	Y
	Y*
	Y
	DO, Plants, Paper accumulation, *blocked supply

	Advising Off. 1
	0
	71
	49
	527
	ND
	5
	N
	Y
	N
	Plants

	Records Clerk
	0
	71
	48
	544
	ND
	6
	N
	Y*
	N
	PF, Plants

	Room 301 (front)
	0
	74
	50
	548
	ND
	6
	N
	Y
	Y
	DO, UF

	Room 301 (hall)
	0
	76
	50
	640
	ND
	8
	N
	Y
	Y

off
	WDCT

	Room 301 A
	0
	74
	47
	452
	ND
	7
	N
	Y
	Y
	DO

	Room 301 C
	0
	73
	51
	448
	ND
	8
	N
	Y
	Y
	DO

	Room 301 Conference
	1
	79
	44
	456
	ND
	8
	Y
	Y
	Y
	AC on wall

	Room 301 D
	1
	75
	51
	742
	ND
	7
	N
	Y
	Y
	DO

	Room 301 E
	1
	72
	49
	439
	ND
	9
	Y
	Y
	Y
	AC on wall; DO

	Room 301 G
	0
	76
	44
	443
	ND
	7
	Y
	Y
	N
	DO

	Room 301 H
	0
	74
	48
	588
	ND
	6
	Y=N
	Y
	Y
	DO

	Room 301 J
	1
	74
	50
	513
	ND
	6
	N
	Y
	Y
	DO

	Room 301 K
	1
	74
	49
	519
	ND
	6
	N
	Y
	Y*
	DO, *backdraft into room

	Room 302
	2
	74
	48
	469
	ND
	7
	N
	Y
	Y
	Water cooler on carpet

	Room 303
	0
	73
	50
	496
	ND
	6
	Y
	Y
	Y*
	*blocked

	Room 303D
	1
	72
	52
	472
	ND
	8
	N
	Y
	N
	DO, DEM, PF, Plants

	Room 306
	7
	74
	48
	525
	ND
	6
	Y
	Y
	Y
	2 DO; CPs; PF; temperature complaints

	Room 309

(mail room side)
	2
	74
	47
	481
	ND
	7
	N
	Y
	
	Passive vent in wall near door; DO

	Room 309 hallway

(to 301 side)
	0
	73
	48
	459
	ND
	7
	N
	Y
	
	Passive vent in wall near door

	Room 404
	2
	73
	49
	548
	ND
	10
	N
	Y
	Y
	PF

	Room 404 A
	2
	73
	48
	483
	ND
	7
	N
	Y
	Y

on wall; blocked
	

	Room 404 F
	1
	72
	49
	464
	ND
	7
	N
	Y
	N
	Kitchen odors; peeling paint; AD on door; microwave; toaster; refrig.; DO

	Room 404E
	0
	73
	49
	537
	ND
	7
	N
	Y
	N
	DO, DEM

	Room 405
	9
	73
	47
	489
	ND
	7
	Y
	Y
	Y
	Plants

	Room 406
	8
	72
	48
	501
	ND
	7
	Y
	Y
	Y
	PC; PF; MT

	Room 406 C
	1
	72
	49
	450
	ND
	7
	N
	Y
	Y
	DO; PF

	Room 406B
	2
	73
	50
	610
	ND
	7
	N
	Y
	Y*
	DO, *blocked, partitions

	Room 406C
	0
	73
	49
	516
	ND
	6
	N
	Y
	N
	DC, partition, exhaust on other side of partition

	Room 407

(reception area)
	3
	73
	47
	475
	ND
	7
	N
	Y
	Y
	CPs; PF; plants; DO

	Room 407 (conference)
	0
	72
	46
	459
	ND
	7
	N
	Y
	N
	DEM; DO; PF

	Room 407 A

(area outside office)
	2
	72
	48
	463
	ND
	7
	N
	Y
	Y

on wall; blocked
	PC; PF; plants

	Room 408 (back)
	2
	73
	45
	529
	ND
	6
	Y
	Y
	Y
	

	Room 408 Entrance


	3


	72


	46


	559


	ND
	6
	Y
	Y

dust
	Y
	Water cooler on carpet; CPs; PF

PC; microwave; Frig.; designjet printer

	Room 416
	0
	74
	46
	693
	ND
	6
	Y
	Y
	Y*
	DC, DEM, *blocked by partitions

	Room 419
	0
	76
	43
	521
	ND
	5
	N
	Y
	Y
	DC, CT ajar, passive vent in door

	Room 419A
	1
	76
	44
	590
	ND
	7
	Y

½ open
	Y*
	Y
	DO, PF

	Room 419B
	1
	75
	45
	684
	ND
	5
	N
	Y*
	Y
	DO, *blocked

	Room 499E
	3
	75
	46
	653
	ND
	7
	N
	Y
	Y
	DC, Broken floor tiles

	Room 504 (Kitchen)
	1
	71
	47
	518
	ND
	8
	N
	N
	N
	Kitchen odors; MTs; WD CTs; Refrig.; Toaster; Microwave

	Room 504 A
	0
	71
	47
	504
	ND
	7
	N
	Y

cardboard
	N
	PF

	Room 504 Comm. (College Kiosk Area)
	3
	69
	50
	494
	ND
	7
	N
	Y
	Y
	Plants on Window sill and on floor; MTs; PF; Kitchen odors; Damaged floor tiles in 504 C; Exhaust vent amd MTs in 504 F

	Room 506
	0
	71
	44
	502
	ND
	6
	Y
	
	
	PF

	Room 508
	1
	71
	48
	862
	ND
	7
	Y
	Y
	N
	

	Room 511
	0
	73
	42
	485
	ND
	7
	Y

1 of 2 open
	Y
	N
	Window AC

	Room 512
	1
	73
	43
	503
	ND
	7
	Y
	
	Y
	Window ACs; WD on wall; subdivided offices along wall with common reception

	Room 514
	2
	76
	43
	494
	ND
	7
	N
	Y

water stains
	N
	CF – on; Plants; water cooler on carpet; DO; temperature control complaints

	Room 514 B
	0
	74
	41
	561
	ND
	6
	N
	N
	N
	PCs; printers

	Room 514 D
	0
	75
	43
	485
	ND
	6
	Y
	Y
	N
	Plants; DO

	Room 514 E
	0
	75
	41
	472
	ND
	6
	N

sealed
	Y
	N
	WD CTs; DO; PF

	Room 517
	4
	73
	43
	490
	ND
	7
	N
	Y
	N
	CF – off; PF; PC; DO

	Room 517 A
	0
	74
	42
	490
	ND
	10
	N
	Y
	N
	CF – off; DO

	Room 517/518 hallway
	
	
	
	
	
	
	
	
	
	WD CTs

	Room 518
	0
	73
	43
	531
	ND
	7
	Y

1 of 1 open
	Y
	N
	WD CTs; DO

	Room 518
	1
	73
	46
	580
	ND
	6
	N
	Y*
	N
	DO, Plants, PF, * blocked

	Room 524
	3
	72
	47
	563
	ND
	6
	Y
	Y
	N
	DO, WC, Plants

	Room 526
	0
	73
	45
	552
	ND
	6
	N
	Y
	N
	DO

	Room 527
	2
	72
	47
	621
	ND
	8
	N
	Y
	N
	DC, CF

	Room 528
	0
	71
	47
	514
	ND
	5
	N
	Y
	N
	DO, Plants

	Room 528A
	2
	71
	48
	590
	ND
	5
	Y
	Y
	N
	DO, PF

	Room 530
	2
	71
	47
	504
	ND
	8
	Y

2/2 open
	Y
	N
	CF, PF, Plants, Stuffed animals

	Room 532 (Lobby)
	0
	71
	47
	583
	ND
	7
	Y
	Y
	N
	DC

	Room 532A
	1
	71
	47
	553
	ND
	9
	Y
	Y
	N
	DO, DEM, Plants

	Room 534 (front)
	2
	72
	47
	613
	ND
	5
	N
	Y
	N
	DC, CF, PF

	Room 534 (graduation)
	2
	73
	45
	641
	ND
	6
	N
	Y
	N
	CF, Plants

	Room 534A
	0
	73
	45
	615
	ND
	6
	N
	Y
	Y
	DO

	Room 536 B
	3
	69
	53
	785
	ND
	7
	Y
	Y
	N
	DO, PF, Plants, insecticide

	Room 538
	5
	72
	48
	639
	ND
	9
	N
	Y
	N
	PF

	Room 538C
	0
	72
	48
	609
	ND
	6
	N
	Y
	Y*
	DO, Plants, PF, *blocked

	Room 602
	1
	73
	44
	481
	ND
	7
	Y
	Y
	N
	DO; plants; PF

	Room 602 A
	1
	73
	43
	478
	ND
	7
	Y

1 of 2 open
	Y
	N
	Plants along window; DO; portable AC off

	Room 604
	0
	72
	47
	459
	ND
	7
	N
	Y
	Y
	WD CTs; MTs; DEM; CD

	Room 608
	2
	72
	46
	514
	ND
	8
	Y

1/3 open
	Y
	Y*
	DO, Plants, WC on carpet, *blocked

	Room 608A
	1
	69
	51
	504
	ND
	7
	Y
	Y
	Y*
	DO, * blocked by partition

	Room 609
	3
	70
	50
	532
	ND
	8
	Y
	Y*
	Y
	DO, blocked by plastic file bin

	Room 609A
	0
	70
	50
	518
	ND
	7
	Y
	Y
	N
	DO

	Room 609B
	1
	70
	51
	553
	ND
	5
	Y
	Y*
	N
	DC, *blocked

	Room 609D
	1
	70
	52
	772
	ND
	6
	Y

2/2 open
	Y
	N
	DO, Plants

	Room 610
	2
	71
	52
	652
	ND
	6
	Y

¼ open
	Y
	Y*
	DO, WC on carpet, * blocked

	Room 612
	2
	72
	44
	521
	ND
	6
	Y
	
	N
	Window AC; plants

	Room 614
	1
	73
	43
	479
	ND
	7
	Y
	
	N
	Window AC; CPs; DEM; DO

	Room 615 (Left side)
	2
	74
	42
	482
	ND
	7
	Y
	Y
	Y
	

	Room 615 (Right side)


	3
	74
	43
	509
	ND
	7
	Y
	Y
	Y
	Window ACs; PF; water cooler on carpet; Frig.; microwave; PC; plants

	Room 615 A
	0
	74
	42
	494
	ND
	8
	Y
	Y
	Y
	Window AC

	Women’s Room
	2
	73
	47
	618
	ND
	8
	Y

1/1 open
	N
	Y
	DC, WD materials, Window cracked


[image: image17.png]PUBLIC HEALTH| H1N1 Flu
FACT SHEET (Swine Flu)

Massachusetts Depariment of Publc Health

WhatIs HIN1 flu?
Fluis  disease of the body's breothing systemn,including the mose,throat and lungs, Fl is short for
“influenza.” HIN fh s caused by a new vinus that was fivst recogaized in April of 2009, sad was called
swine flu” HINI flu quickly spread to many pasts o the world snd is now o “pandemic.” o global
outbresk. HINI flu s not the same as svine f, which is o virus that pgs can get. It s not the same a5
<easonal” i which oceurs every year, during the winter and early spring. But HINI flu canses symptoms
hat e similr to seasanal . is spread like seasonsl i, and can be prevented like seasonal fu.

What are the symptoms of HIN1 flu?

FINT flu symptomss s very similar to seasonal lu syanptoms. Most common sre fever, cough, and sore

theoat. Symptoms can also include body aches, headache. chills, iy nose and fecling very tired. Some
e aleo have disrhen snd vomiting. Symptoms last from o few days to up to a week or more.

Is HIN1 flu serious?
iness with HINL flu has ranged from mild o severe. While most people sick with HIN1 flu get betier
sithont needing medical trestment,severe illness and deaths have ocerured in some people. Like seasonal
i, some people are at higher sk of serious health problems when they get the HINT flu, This includes
prezaan women, infants, and people with medical condirions like asthma, didberes, heart discase, kidacy
discase, musele or nerve conditions that affect their breathing and weakened immune systems.





[image: image18.png]How does H1N1 fiu spread?
The flu virus s in the wet spray (droplets of saliva and scous) that comes out of the nose and mouth of
someone who coughs o sneszes. [f you are close enough o a person with the lu (3 - 6 fet) when they
cough or sneeze, you can breathe in the virus and g sick. FIu symptoms stact 1 - 4 days (usually 2 days)
aftera person breathes i the virus

Fhnis spread sasily from pesson fo person. The virus can also live for a shorttme on things yon touch ike
dootknobs, phones and fays. After you foneh these objeets, you ean cateh the virus when you touch your
‘mourh, nose, or eyes. However, when the wet droplets o hese types of objects dry our, the virus can't
Cause infection. Adults with the HIN flu can spread it from about one day before symplomas appeas to
about one week afcr. Childsen can spread the flu even longer after they get sick.

How is HIN1 flu treated?
There are drugs availsble that your doctor may prescribe to treat HIN flu. The drugs work best if started
soon afte the sart of symptoms. Your doctor can determine if you need treatment

‘People sick with any type of fu should make sure to drink pleaty of Quids. get plenty ofsest, <ot healthy
foods. wash theis bands frequently anc stay home to avoid spreading the fu o othes people. Over the
counter pain selievers may bielp people with the flu feel smore comfortable. Children aud teens with the
“hould never take aspirin, because a rare but serious disease called Reye syndrome can oceur

Is there a vaccine for HTN1 flu?
Ves. A vaccine helps your body to protest itelf against  disease. There are fwo types of HINT vaceine
avilble o protect agninst HINT flu. One is o “shot” that is given with a needle. wsually n the arm. The
other s “asal spray” (s spray inbaled throngh the nose). Peaple 10 years of age sad over will need one





19

[image: image19.png]dose of vaceine. Most children under the age of 10 will nced two doses of HINI vaceiue, sepauted by 3- 4
srecks. Geting fln vaceine will not give you the lu or any other fype of dlacss. Ask your doctor which
type of HINI vaceine s best for you and your Family

Who should get HIN1 flu vaccine?
Cerain groups should get the HINI vascine when it becomes available: pregnant womens: people wh live
with or provide care for infants under 6 months of age (c.2., pareats, siblings, and dayeare providers):
healtheare and emeraeney medical services personncl; people age 6 months 10 24 years: and people age 25
0 61 sears who have medical conditions hat put them at higher rik for influenza-related complications.
Afier these groups, it is expected thatthere will be cnough HIN1 flu vaceine for anyone who chooses fo g<t
vaceinated. Please note that the aroups listed above may change based on vaceine availabilty. Note
current studies indicate the sk for ifection among persons over 65 vears of age s les than he risk for
persans in younger age groups

How do | know f I have H1NA flu?
1Fyou have symptonas of fl, it could be seasonal or HINT flu. If you think you Lave the flu, stay home
from work nud sciool and avoid cotact with oters s0 you do not spread the virus. If you thiak you might
ave fh an you need to sce your doctor, call aiead and let them knon yon might have the . That w
office can take seps to avoid the spread of o others. The doctor may recommend fhat yors

How do | protect myself from getting sick with HIN1 flu?

« Get vaceinated when the vaceine becomes available, especially if you have a medical condition which
makes health complicarions from the ln more likely.

 Wash your hands often with soap and water or use alcohol based hand gel.

« Cough or suceze into a tissue or the inside of your elbow i you don't bave a tissue, Thow the tissue in
the trash s wash your hads.

 Usea segular household cleaner o clean susfaces that uight get £ vizus on themn Like doos kiobs, phones,
faucets and toys.




