The Commonwealth of Massachusetts

Executive Office of Health and Human Services

Department of Public Health

Bureau of Climate and Environmental Health

Community Sanitation Program

67 Forest Street, Suite # 100

Marlborough, MA 01752

Phone: 857-507-7205

KATHLEEN E. WALSH

Secretary

ROBERT GOLDSTEIN, MD, PhD Commissioner

Tel: 617-624-6000

www.mass.gov/dph

MAURA T. HEALEY

Governor

KIMBERLEY DRISCOLL

Lieutenant Governor

April 30, 2024

Jason Rives, Superintendent

Worcester County House of Corrections and Jail

5 Paul X. Tivnan Drive

West Boylston, MA 01583		(electronic copy)

Re: Facility Inspection – Worcester County House of Corrections and Jail, West Boylston

Dear Superintendent Rives:

In accordance with M.G.L. c. 111, §§ 5, 20, and 21, as well as Massachusetts Department of Public Health (Department) Regulations 105 CMR 451.000: Minimum Health and Sanitation Standards and Inspection Procedures for Correctional Facilities; 105 CMR 480.000: Minimum Requirements for the Management of Medical or Biological Waste (State Sanitary Code, Chapter VIII); 105 CMR 590.000: Minimum Sanitation Standards for Food Establishments (State Sanitary Code Chapter X); the 2013 Food Code; 105 CMR 500.000 Good Manufacturing Practices for Food; and 105 CMR 205.000 Minimum Standards Governing Medical Records and the Conduct of Physical Examinations in Correctional Facilities; the Department’s Community Sanitation Program (CSP) conducted an inspection of the Worcester County House of Corrections and Jail on April 5 and 8, 2024 accompanied by Noe Bard, Environmental Health and Safety Officer and Terrance Ward, Fire Safety Officer. Violations noted during the inspection are listed below including 154 repeat violations:

Should you have any questions, please don’t hesitate to contact me.

Sincerely,

Amy Medeiros

Environmental Health Inspector, CSP, BCEH

cc: 	Robert Goldstein, MD, PhD, Commissioner, DPH

Nalina Narain, Director, BCEH

Steven Hughes, Director, CSP, BCEH

Kathleen E. Walsh, Secretary, Executive Office of Health and Human Services	(electronic copy)

Carol A. Mici, Commissioner, DOC   						(electronic copy)

Terrence Reidy, Secretary, EOPSS						(electronic copy)

Brianna Arruda, Director, Policy Development and Compliance Unit 		(electronic copy)

Noe Bard, Environmental Health and Safety Officer				(electronic copy)

Terrance Ward, Fire Safety Officer						(electronic copy)

Diane M. Cook, Compliance Analyst						(electronic copy)

Margaret Lee, Administrative Assistant, West Boylston Board of Health		(electronic copy)

Clerk, Massachusetts House of Representatives					(electronic copy)

Clerk, Massachusetts Senate							(electronic copy)

HEALTH AND SAFETY VIOLATIONS

(* indicates conditions documented on previous inspection reports)

Entrance

Superintendent’s Office

No Violations Noted

Waiting Area

No Violations Noted

Fisher Conference Room

No Violations Noted

Operations Office

No Violations Noted

Communication Director’s Office

Unable to Inspect – Locked

Male Staff Locker Room

105 CMR 451.353*	Interior Maintenance: Ceiling tiles water damaged

Male Staff Bathroom

105 CMR 451.123*	Maintenance: Heater damaged

Female Changing Area

No Violations Noted

Control Room

No Violations Noted

Control Bathroom

105 CMR 451.123*	Maintenance: Ceiling vent dusty

Key Room

No Violations Noted

Herman Building

VISITING ROOM

Non-Inmate Visiting Side

No Violations Noted

Female Handicapped Bathroom

No Violations Noted

Male Handicapped Bathroom

No Violations Noted

Female Bathroom

No Violations Noted

Male Bathroom

105 CMR 451.123	Maintenance: Wall paint damaged above urinal

Inmate Visiting Side

105 CMR 451.353*	Interior Maintenance: Countertop damaged in booth # 1, 10, 12, and 14

Father’s Visiting Room

No Violations Noted

Old Receiving

Old County Lockup

Unable to Inspect – Not Used

Property

No Violations Noted

Breakroom & Bathroom

105 CMR 451.123	Maintenance: Walls dirty in Bathroom

Utility Closet

No Violations Noted

Offices

105 CMR 451.353*	Interior Maintenance: Ceiling vent blocked in Parole Office

Central Control

No Violations Noted

Control Bathroom

105 CMR 451.123*	Maintenance: Ceiling tile missing

A1 Block

105 CMR 451.320*	Cell Size: Inadequate floor space in all cells

Control Booth

No Violations Noted

Control Bathroom

No Violations Noted

Day Room

No Violations Noted

Room # 1

No Violations Noted

Room # 2

No Violations Noted

Room # 3

No Violations Noted

Storage # 4

No Violations Noted

Storage # 5

No Violations Noted

Shakedown Room # 6

No Violations Noted

Slop Sink (Upstairs)

No Violations Noted

Cells (Upstairs)			Unable to Inspect Cell # 16 – Not Used

105 CMR 451.360*	Protective Measures: Birds nest observed in window in cell # 10

105 CMR 451.360	Protective Measures: Birds nest observed in window in cell # 7, 6, and 9

Showers (Upstairs)

No Violations Noted

Slop Sink (Downstairs)

No Violations Noted

Cells (Downstairs)

105 CMR 451.353                      Interior Maintenance: Wall vent blocked in cell # 30

105 CMR 451.360	Protective Measures: Birds nest observed in window in cell # 24

Showers (Downstairs)

105 CMR 451.123	Maintenance: Ceiling vent dusty in shower # 2

Rec Area

No Violations Noted

A2 Block

105 CMR 451.320*	Cell Size: Inadequate floor space in all cells

Control Booth

No Violations Noted

Control Bathroom

105 CMR 451.117*	Toilet Fixtures: Toilet fixture dirty

105 CMR 451.123*	Maintenance: Ceiling vent dusty

Day Room

No Violations Noted

Chemical Storage Room

No Violations Noted

Paper Goods Storage

No Violations Noted

Staff Room

No Violations Noted

Slop Sink Room (Upstairs)

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, slop sink out-of-order

Cells (Upstairs)

No Violations Noted

Showers (Upstairs)		Unable to Inspect Shower # 2 – In Use

105 CMR 451.123	Maintenance: Soap scum on walls in shower # 1

Slop Sink (Downstairs)

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, slop sink clogged

Cells (Downstairs)

No Violations Noted

Showers (Downstairs)

Unable to Inspect – In Use

Hallway

Storage Closets

Unable to Inspect – Locked

MAXI B

105 CMR 451.320*			Cell Size: Inadequate floor space in all cells

Control

No Violations Noted

Control Bathroom

105 CMR 451.123*	Maintenance: Floor paint damaged

105 CMR 451.123	Maintenance: Floor and walls dirty

Lower Right Tier

Day Room

No Violations Noted

Chemical Storage

No Violations Noted

Showers			Unable to Inspect Shower # 2 – In Use

105 CMR 451.123*	Maintenance: Wall paint and epoxy damaged in shower # 1

105 CMR 451.123*	Maintenance: Mold on walls in shower # 1

Cells

105 CMR 451.353	Interior Maintenance: Floor paint damaged in cell # 124

105 CMR 451.353*	Interior Maintenance: Seat missing at desk in cell # 142

105 CMR 451.353                      Interior Maintenance: Wall vent blocked in cell # 130 and 142

Lower Left Tier

Day Room

No Violations Noted

Cells

105 CMR 451.353	Interior Maintenance: Floor paint damaged in cell # 123 and 127

105 CMR 451.353                      Interior Maintenance: Wall vent blocked in cell # 107, 115, 129, 133, 135, 139, and 151

Showers

Unable to Inspect – In Use

Slop Sink

No Violations Noted

Chemical Closet

No Violations Noted

Lower Disciplinary Unit	Unable to Inspect – Not Used

105 CMR 451.350	Structural Maintenance: Exterior door not rodent and weathertight outside Lower Disciplinary Unit

Upper Right Tier

Day Room

105 CMR 451.346*	Safe Wiring: Inappropriate use of temporary wiring, industrial fan cord extended through doorway from cell block

105 CMR 451.353*	Interior Maintenance: One seat missing at table

Cells

105 CMR 451.353                      Interior Maintenance: Wall vent blocked in cell # 316, 342, and 352

Slop Sink

No Violations Noted

Showers

105 CMR 451.123*	Maintenance: Soap scum on curtain in shower # 1

105 CMR 451.123*	Maintenance: Wall paint and epoxy damaged in shower # 1 and 2

Upper Disciplinary Unit	Unable to Inspect Cell # 4 – Not Used

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, toilet push button leaking in cell # 3

105 CMR 451.353*	Interior Maintenance: Wall paint damaged in cell # 3

Upper Left Tier

Day Room

105 CMR 451.346	Safe Wiring: Inappropriate use of temporary wiring, industrial fan cord extended through doorway from cell block

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged outside Day Room

Slop Sink

No Violations Noted

Cells

105 CMR 451.353*	Interior Maintenance: Floor paint damaged in cell # 309, 325, 333, and 335

105 CMR 451.353	Interior Maintenance: Floor paint damaged in cell # 313

105 CMR 451.353                      Interior Maintenance: Wall vent blocked in cell # 309

Showers

Unable to Inspect – In Use

Slop Sink

No Violations Noted

Chapel

No Violations Noted

Offices

Unable to Inspect – Locked

Food Service

The following Food Code violations listed in BOLD were observed to be corrected on-site.

Staff Dining & Culinary

Staff Dining Room

No Violations Noted

Staff Serving Line & Prep Area

No Violations Noted

Pots & Pans Culinary Closet

FC 6-501.12(A)	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not cleaned as often as necessary, mouse droppings observed

Handwash Sink

No Violations Noted

Ovens & Hood

No Violations Noted

Main Kitchen

Handwash Sink

FC 7-102.11                                Labeling and Identification, Working Containers: Working container of poisonous/toxic materials missing common name of materialPf, soap used in sanitizer buckets

Food Prep Area

FC 3-304.12(B)	Protection from Contamination After Receiving; Preventing Contamination from Equipment, Utensils, and Linens: Utensil handle not stored above the food in the container, scoop in ice machine

FC 6-501.12(A)	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not cleaned as often as necessary, floor dirty behind ovens

Kettles & Hood

No Violations Noted

Handwash Sink

No Violations Noted

Milk Cooler # 1

No Violations Noted

Produce Cooler # 2

FC 6-501.12(A)	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not cleaned as often as necessary, fan dirty

Tool Storage Closet

FC 6-501.12(A)	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not cleaned as often as necessary, rotten apple on floor

Prep Cooler # 3

FC 6-501.11*	Maintenance and Operation; Repairing: Facility not in good repair, floor tiles damaged

Freezer

No Violations Noted

Dry Goods

FC 6-501.12(A)	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not cleaned as often as necessary, mouse droppings observed

Control

No Violations Noted

Control Bathroom

No Violations Noted

Entry 5 Area (Near Dry Goods)

No Violations Noted

Receiving Area

No Violations Noted

Chemical Closet

FC 5-205.15(B)*	Plumbing System; Operation and Maintenance: Plumbing system not maintained in good repair, backflow preventor leaking

Dishwasher Area

FC 6-501.11*	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not in good repair, ceiling paint damaged above warewash machine

FC 4-501.15	Maintenance and Operation; Equipment: Warewashing machine not operating in accordance with manufacturer's instructions, final rinse temperature low

FC 6-501.12(A)	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not cleaned as often as necessary, mouse droppings observed

3-Compartment Sink # 1 and 2

No Violations Noted

Culinary Dry Goods

FC 3-304.12(B)	Protection from Contamination After Receiving; Preventing Contamination from Equipment, Utensils, and Linens: Utensil handle not stored above the food in the container, scoop in oats

Exterior Door

No Violations Noted

Kitchen Dry Goods

FC 6-501.12(A)*	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not cleaned as often as necessary, mouse droppings observed

FC 6-501.112	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Dead or trapped pests not removed from controlled devices, mouse in trap

Inmate Serving Area

FC 2-301.14*	Hands and Arms: Food employees not washing hands prior to engaging in food preparationP

FC 2-402.11*	Hygienic Practices; Hair Restraints: Food service personnel not wearing appropriate hair restraints, beard guards and hair nets missing

Inmate Bathroom

105 CMR 451.123*	Maintenance: Door frame damaged

Main Gymnasium

Slop Sink Closet (Hallway)

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, drain cover missing

105 CMR 451.353*	Interior Maintenance: Ceiling vent dusty

Basketball Court

105 CMR 451.350*	Structural Maintenance: Floor damaged

105 CMR 451.350*	Structural Maintenance: Walls damaged

105 CMR 451.350*	Structural Maintenance: Ceiling damaged

105 CMR 451.353*	Interior Maintenance: Ceiling paint damaged

Inmate Toilets & Showers 	Unable to Inspect Showers – Not Used

105 CMR 451.123*	Maintenance: Ceiling vent dusty above toilets

Booth

105 CMR 451.200*	Food Storage, Preparation and Service: Food storage not in compliance with                105 CMR 590.000, refrigerator gaskets damaged

105 CMR 451.353*	Interior Maintenance: Floor tiles damaged

Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling vent dusty

105 CMR 451.123*	Maintenance: Door stuck and difficult to open

Bathroom without Showers

Unable to Inspect – Closed

MAXI C

105 CMR 451.320*	Cell Size: Inadequate floor space in all cells

Control Booth

No Violations Noted

Booth Bathroom

105 CMR 451.123*	Maintenance: Ceiling vent dusty

Upper Tier

Left-Side Day Room

105 CMR 451.344*	Illumination in Habitable Areas: Light not functioning properly, 3 lights out

105 CMR 451.200*	Food Storage, Preparation and Service: Food preparation not in compliance with          105 CMR 590.000, interior of microwave oven dirty

Right-Side Day Room

105 CMR 451.353*	Interior Maintenance: One seat missing at table

Cells				Unable to Inspect Cell # 450 – Under Construction

105 CMR 451.350*	Structural Maintenance: Window broken in cell # 403

105 CMR 451.353*	Interior Maintenance: Wall paint damaged in cell # 409

105 CMR 451.353	Interior Maintenance: Floor paint damaged in cell # 412

105 CMR 451.353	Interior Maintenance: Trash and debris on floor in cell # 433 and 437

105 CMR 451.353*	Interior Maintenance: Seat and desk missing in cell # 449

Showers

105 CMR 451.123*	Maintenance: Epoxy damaged in shower # 1, 2, and 3

105 CMR 451.123*	Maintenance: Mold on walls in shower # 1, 2, and 3

Slop Sink

No Violations Noted

Old Segregation

Unable to Inspect – Not Used

Lower Tier

Left-Side Day Room

No Violations Noted

Right-Side Day Room

105 CMR 451.353	Interior Maintenance: One seat missing at tables

Cells

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 230, 232, and 247

105 CMR 451.353	Interior Maintenance: Wall damaged in cell # 227

Slop Sink

No Violations Noted

Showers

105 CMR 451.123*	Maintenance: Ceiling paint damaged outside showers

105 CMR 451.123*	Maintenance: Wall paint and epoxy and paint damaged in shower # 1, 2, and 3

105 CMR 451.123*	Maintenance: Mold on walls in shower # 1, 2, and 3

105 CMR 451.123	Maintenance: Ants observed in shower # 1

Segregation

Unable to Inspect – Not Used

Chemical Area

No Violations Noted

Programs

Offices

No Violations Noted

Break Area in Hall

No Violations Noted

Male Staff Bathroom

No Violations Noted

Classrooms

No Violations Noted

Female Staff Bathroom

No Violations Noted

Slop Sink Room

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, drain cover damaged at slop sink

Library

No Violations Noted

Maintenance Corridor

Staff Bathroom

No Violations Noted

Inmate Bathroom

No Violations Noted

Office with Bathroom

No Violations Noted

Laundry Area

No Violations Noted

Tool Crib

No Violations Noted

Electrical Shop

No Violations Noted

Maintenance Break Room

No Violations Noted

Welding Area

No Violations Noted

EHSO Office (Waste Log)

No Violations Noted

Captain/Lieutenant’s Office Area

Old Cells/Biohazard Storage

Unable to Inspect – Not Used

Lieutenant’s Cubicles

No Violations Noted

Lieutenant’s Bathroom

No Violations Noted

Offices

No Violations Noted

Bathrooms (2)

105 CMR 451.123*	Maintenance: Wall damaged under handwash sink in bathroom # 1

Slop Sink

No Violations Noted

Break Area

No Violations Noted

Deignan Building

105 CMR 451.320*	Cell Size: Inadequate floor space in all cells

Control Booth

105 CMR 451.353*	Interior Maintenance: Floor paint damaged

105 CMR 451.350	Structural Maintenance: Window damaged

Control Booth Bathroom

No Violations Noted

Common Area

105 CMR 451.141*	Screens: Screen missing

105 CMR 451.340*	Illumination: Insufficient lighting, lights out

105 CMR 451.353*	Interior Maintenance: Ceiling fans dusty

105 CMR 451.353*	Interior Maintenance: One ceiling fan out-of-order

Mental Health Office

No Violations Noted

Dry Storage

No Violations Noted

Chemical Closet

No Violations Noted

Upper West

Showers

No Violations Noted

Cells

105 CMR 451.350*	Structural Maintenance: Window broken in cell # 49 and 55

Slop Sink Room

No Violations Noted

Bathroom

105 CMR 451.123*	Maintenance: Basin damaged at handwash sink # 1

105 CMR 451.126*	Hot Water for Bathing and Hygiene: No hot water supplied to handwash sink # 3

105 CMR 451.123	Maintenance: Partition paint damaged in toilet stall # 2

Lower West

Showers

105 CMR 451.123*	Maintenance: Drain flies observed in shower # 2

105 CMR 451.123*	Maintenance: Light rusted in shower # 2

105 CMR 451.123	Maintenance: Soap scum on curtain in shower # 2

Bathroom

105 CMR 451.123*	Maintenance: Basin damaged at handwash sink # 1

105 CMR 451.123*	Maintenance: Floor damaged

105 CMR 451.123*	Maintenance: Heater rusted

105 CMR 451.123*	Maintenance: Partition paint damaged in toilet stall # 1

Cells

No Violations Noted

Lower East

Showers

105 CMR 451.123*	Maintenance: Soap scum on curtain in shower # 1

105 CMR 451.123	Maintenance: Soap scum on curtain in shower # 2

Bathroom

105 CMR 451.123*	Maintenance: Floor paint damaged

Cells

105 CMR 451.350*	Structural Maintenance: Window broken in cell # 14

Slop Sink Room

No Violations Noted

Upper East

Slop Sink Room

No Violations Noted

Cells

105 CMR 451.350*	Structural Maintenance: Windowpane cracked in cell # 23 and 32

Showers

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower # 2 out-of-order

Bathroom

105 CMR 451.123*	Maintenance: Floor paint damaged

105 CMR 451.123*	Maintenance: Heater rusted

105 CMR 451.123	Maintenance: Partition paint damaged in toilet stall # 1

Mini 5 Building

Unable to Inspect – Under Construction

Modular Administration Building

Lobby

Waiting Area

No Violations Noted

Male Bathroom

105 CMR 451.123*	Maintenance: Floor damaged

Female Bathroom

105 CMR 451.123*	Maintenance: Wall tiles damaged

Mail Room

No Violations Noted

Control 3

105 CMR 451.353*	Interior Maintenance: Floor damaged throughout Control 3

Control Bathroom

105 CMR 451.123*	Maintenance: Floor tiles missing and damaged

105 CMR 451.123*	Maintenance: Exposed plywood floor water damaged

105 CMR 451.123*	Maintenance: Wall tile damaged behind toilet

Special Services Corridor

105 CMR 451.353*	Interior Maintenance: Floor tiles damaged in hallway

Offices

105 CMR 451.353	Interior Maintenance: Mold on ceiling tiles around ceiling vent in hallway

Female Bathroom

No Violations Noted

Slop Sink Room

Unable to Inspect – Locked

Male Bathroom

105 CMR 451.123	Maintenance: Floor tiles damaged

Female Locker Room

105 CMR 451.123*	Maintenance: Floor dirty in shower # 2 and handicapped shower

105 CMR 451.123*	Maintenance: Wall damaged in handicapped shower

105 CMR 451.123*	Maintenance: Walls dirty in handicapped shower

105 CMR 451.123	Maintenance: Ceiling leaking

Male Locker Room & Bathroom

105 CMR 451.123*	Maintenance: Ceiling dirty near ceiling vents in changing area, possible mold

105 CMR 451.123*	Maintenance: Floor and bench dirty in handicapped shower

105 CMR 451.123*	Maintenance: Ceiling vent dusty

105 CMR 451.123*	Maintenance: Floor dirty in shower # 2

105 CMR 451.123*	Maintenance: Curtains dirty in shower # 1, 2, 3, 4, and 5

Staff Training Room A & B

No Violations Noted

Special Services Office

Unable to Inspect – Locked

2nd Floor

Personnel Offices

No Violations Noted

Break Room

No Violations Noted

Copy Room

Unable to Inspect – Locked

North Male Bathroom (near slop sink)

105 CMR 451.126		Hot Water for Bathing and Hygiene: Hot water temperature 1460F at handwash sink

Slop Sink Room

Unable to Inspect – Locked

North Female Bathroom (near slop sink)

No Violations Noted

South Male Bathroom

No Violations Noted

South Female Bathroom

105 CMR 451.123	Maintenance: Ceiling vent dusty

Internal Affairs

Unable to Inspect – Locked

Trap

Pedestrian Trap

105 CMR 451.353	Interior Maintenance: Floor tiles damaged

Bathroom in Pedestrian Trap

105 CMR 451.123*	Maintenance: Ceiling damaged

Visits Waiting Area

105 CMR 451.353*	Interior Maintenance: Floor tiles damaged

Modular Gym

Inmate Bathroom # 104

105 CMR 451.123*	Maintenance: Light out

105 CMR 451.123*	Maintenance: Floor tile missing

105 CMR 451.123*	Maintenance: Ceiling vent cover missing

105 CMR 451.123*	Maintenance: Wall damaged

Staff Bathroom # 105

No Violations Noted

Mop Closet/Electrical # 106

No Violations Noted

Storage Room # 108

No Violations Noted

Gym

105 CMR 451.141*	Screens: Several screens damaged

105 CMR 451.350*	Structural Maintenance: Back door not rodent and weathertight

Control # 102

No Violations Noted

Trailer # 1 (Attorney Visits)

No Violations Noted

Trailer # 2 (Lieutenant Offices)

Unable to Inspect – Locked

Trailer # 3

Unable to Inspect – Locked

Modular Visiting Area

Unable to Inspect – Closed

VOC & Laundry

Unable to Inspect – Under Construction

H Building

105 CMR 451.320*	Cell Size: Inadequate floor space in all cells

105 CMR 451.350*	Structural Maintenance: Exterior wall damaged

Control Booth

No Violations Noted

Control Bathroom

No Violations Noted

Common Area

No Violations Noted

Showers

No Violations Noted

Office

No Violations Noted

Cells

105 CMR 451.350*	Structural Maintenance: Unable to open or close cell windows

Chemical Room

Unable to Inspect – Locked

I Building

105 CMR 451.350	Structural Maintenance: Exterior wall damaged

Control Booth

105 CMR 451.353*	Interior Maintenance: Ceiling tiles water damaged

Control Bathroom

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1010F at handwash sink

Common Area

105 CMR 451.200	Food Storage, Preparation and Service: Food preparation not in compliance with          105 CMR 590.000, interior of microwave ovens dirty

Showers

105 CMR 451.123	Maintenance: Floor dirty in shower # 4

105 CMR 451.123	Maintenance: Paint damaged on column in shower # 3, 4, and 6

105 CMR 451.123	Maintenance: Walls dirty in shower # 8

105 CMR 451.123	Maintenance: Soap scum on walls in shower # 9

105 CMR 451.130	Hot Water: Shower water temperature recorded at 1200F in shower # 10

105 CMR 451.123	Maintenance: Wall epoxy worn in shower # 2, 4, 5, 8, 9, and 10

Office

No Violations Noted

Cells

105 CMR 451.350*	Structural Maintenance: Unable to open or close cell windows

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 177

105 CMR 451.353*	Interior Maintenance: Seat missing at desk in cell # 196 and 203

105 CMR 451.353*	Interior Maintenance: Wall paint damaged in cell # 194 and 196

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 192 and 209

105 CMR 451.353                      Interior Maintenance: Wall vent blocked in cell # 172, 189, 201, 215, and 218

Chemical Room

Unable to Inspect – Locked

J Building

105 CMR 451.350*	Structural Maintenance: Black substance on exterior of building

Common Area

105 CMR 451.353*	Interior Maintenance: One seat cover damaged

Showers

No Violations Noted

Interview Room

No Violations Noted

Cells

105 CMR 451.350*	Structural Maintenance: Unable to open or close cell windows

105 CMR 451.350	Structural Maintenance: Window frame not weathertight, paper towels stuffed into window frame in cell # 245

105 CMR 451.353	Interior Maintenance: Wall vent blocked in cell # 224, 226, 232, 242, 249, 257, and 260

105 CMR 451.353*	Interior Maintenance: Seat missing at desk in cell # 265

Chemical Room

No Violations Noted

K Building

105 CMR 451.320*	Cell Size: Inadequate floor space in all cells

105 CMR 451.350*	Structural Maintenance: Black substance on exterior of building

Control Booth

105 CMR 451.350*	Structural Maintenance: Window in door broken

Control Bathroom

No Violations Noted

Common Area

No Violations Noted

Showers

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower # 10 leaking

105 CMR 451.123	Maintenance: Walls dirty in shower # 3, 4, 5, 7, 8, and 9

Cells

105 CMR 451.350*	Structural Maintenance: Unable to open or close cell windows

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 286

Chemical Room

No Violations Noted

L Building

105 CMR 451.320*	Cell Size: Inadequate floor space in all cells

105 CMR 451.350*	Structural Maintenance: Black substance on exterior of building

105 CMR 451.350*	Structural Maintenance: Window broken in trap

Common Area

No Violations Noted

Showers

105 CMR 451.123*	Maintenance: Wall paint damaged in shower # 7

105 CMR 451.123	Maintenance: Wall paint damaged in shower # 4, 6, 8, 9, and 10

Interview Room

No Violations Noted

Cells

105 CMR 451.350*	Structural Maintenance: Unable to open or close cell windows

105 CMR 451.353	Interior Maintenance: Wall water damaged under window in cell # 353

105 CMR 451.350	Structural Maintenance: Window frame not weathertight, paper towels stuffed into window frame in cell # 347 and 363

105 CMR 451.350*	Structural Maintenance: Windows not weathertight, plastic on window in cell # 370

105 CMR 451.350	Structural Maintenance: Windows not weathertight, plastic on window in cell # 359

105 CMR 451.353		Interior Maintenance: Wall vent blocked in cell # 374, 377, and 385

105 CMR 451.350	Structural Maintenance: Windows not weathertight, window leaking in cell # 395

Chemical Room

No Violations Noted

MIU

Receiving

Holding Cells

No Violations Noted

Staff Bathroom

No Violations Noted

Receiving Trap

No Violations Noted

Interview Room

No Violations Noted

Classification Hearings # 109

No Violations Noted

Medical Intake # 108

Unable to Inspect – Locked

Medical Exam Room # 107

Unable to Inspect – Locked

Search and Changing Rooms

105 CMR 451.130	Hot Water: Shower water temperature recorded at 660F in shower # 104B

Medical Offices

No Violations Noted

Booking Station

No Violations Noted

Offices

No Violations Noted

Bathrooms # 126 and 127

No Violations Noted

Bathrooms # 151 and 152

No Violations Noted

Medical Supply Storage Closet # 150

Unable to Inspect – Locked

Conference Room # 149

Unable to Inspect – Locked

Janitor’s Closet # 154

Unable to Inspect – Locked

Janitors Closet # 146

Unable to Inspect – Locked

Medical Entrance

No Violations Noted

Right Wing

Inmate WC # 166

Unable to Inspect – Not Used

Dental # 165

No Violations Noted

Janitor’s Closet # 164

Unable to Inspect – Locked

Exam 1 # 162

No Violations Noted

Exam 2 # 161

No Violations Noted

Exam 3 # 160

No Violations Noted

Waiting Area 1 # 152

No Violations Noted

Nurse’s Station

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, handwash sink faucet loose

Left Wing

Waiting Area 2 # 158

No Violations Noted

Interview Room # 178

No Violations Noted

Exam 4 # 177

No Violations Noted

Exam 5 # 176

No Violations Noted

Breakroom # 175

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 740F at handwash sink

Exam 6 # 174

No Violations Noted

Minor Proc # 173

Unable to Inspect – Locked

Medical Storage # 172

No Violations Noted

Clean Storage # 171

No Violations Noted

Soil Storage # 170 (Medical Waste)

No Violations Noted

Inmate WC # 169

No Violations Noted

2nd Floor

Staff WC

No Violations Noted

Storage Closets

No Violations Noted

Showers			Unable to Inspect Shower # 1 – Not Used

105 CMR 451.123*	Maintenance: Soap scum on walls and floor in shower # 3

Group Rooms

Unable to Inspect – In Use

Single Cells

No Violations Noted

Work Release

Unable to Inspect – Closed

Tower

Unable to Inspect – Closed

Warehouse Building (outside)

Staff Gym

Weight Area

No Violations Noted

Female Bathroom/Locker Room

105 CMR 451.123*	Maintenance: Floor tiles not secured by toilet

Male Bathroom /Locker Room

No Violations Noted

Chemical Room

Unable to Inspect – Locked

Office

Unable to Inspect – Locked

Warehouse

The following Food Code violations listed in BOLD were observed to be corrected on-site.

Office

No Violations Noted

Staff Bathroom # 1

No Violations Noted

Staff Bathroom # 2

105 CMR 451.123*	Maintenance: Wall paint damaged

105 CMR 451.123*	Maintenance: Floor tile damaged

105 CMR 451.123*	Maintenance: Walls dirty

Chemical Room

No Violations Noted

Walk-In Freezer

FC 4-501.11(A)*	Maintenance and Operation, Equipment: Equipment not maintained in a state of good repair, 1 fan out-of-order in freezer

Dry Storage Closet

FC 6-501.11*	Maintenance and Operation; Premises, Structure, Attachments, and Fixtures - Methods: Facility not in good repair, ceiling damaged

Exterior Cooler # 1

No Violations Noted

Exterior Cooler # 2

No Violations Noted

IT Trailer

No Violations Noted

Garage/Transport

Transportation Office

No Violations Noted

Kitchen Area

No Violations Noted

Bathroom # 1

No Violations Noted

Bathroom # 2

No Violations Noted

Tool Room

No Violations Noted

Wash Room

No Violations Noted

Garage Room

No Violations Noted

Key Control

No Violations Noted

Annex

No Violations Noted

Visitation Area

No Violations Noted

Control

No Violations Noted

Control Bathroom

No Violations Noted

Staff Bathroom # 1

No Violations Noted

Staff Bathroom # 2

105 CMR 451.126		Hot Water for Bathing and Hygiene: Hot water temperature 800F at handwash sink

Chemical Closet

No Violations Noted

Social Worker Office

No Violations Noted

Storage Closet

No Violations Noted

Showers

105 CMR 451.123	Maintenance: Wall paint damaged in shower # 4

Toilet/Handwash Sink Units

Unable to Inspect – Under Construction

Handwash Sink Area

Unable to Inspect – Under Construction

Classrooms

105 CMR 451.124	Water Supply: Excessive water supply in quantity and pressure at water fountain

Sleeping Area

No Violations Noted

Inmate Refrigerator

No Violations Noted

Inmate Laundry

No Violations Noted

Observations and Recommendations

- The inmate population was 689 at the time of inspection.

- At the time of inspection, the Mini 5 Building, VOC/Laundry, Work Release, and Tower were closed and not in use.

- During the kitchen inspection, the warewash machine did not reach the appropriate temperature to properly sanitize trays. As an interim measure, it was stated that Styrofoam trays would be used, manual washing and sanitizing of dishes would occur, and a service call would be placed.

- The cell windows in H, I, J, K, and L Building have deteriorated and are no longer able to be opened or closed from the window controls. The CSP is concerned the windows do not continuously operate as designed and recommends initiating a plan to replace or repair the windows to ensure they are operable and weathertight.

This facility does not comply with the Department’s Regulations cited above. In accordance with 105 CMR 451.404, please submit a plan of correction within 10 working days of receipt of this notice, indicating the specific corrective steps to be taken, a timetable for such steps, and the date by which correction will be achieved. The plan should be signed by the Superintendent or Administrator and submitted to my attention, at the address listed above.

To review the specific regulatory requirements please visit our website at www.mass.gov/dph/dcs and click on "Correctional Facilities" (available in both PDF and RTF formats).

To review the Food Establishment Regulations or download a copy, please visit the Food Protection website at www.mass.gov/dph/fpp and click on "Retail food". Then under DPH Regulations and FDA Code click "Merged Food Code" or "105 CMR 590.000 - State Sanitary Code Chapter X - Minimum Sanitation Standards for Food Establishments".

To review the Labeling regulations please visit the Food Protection website at www.mass.gov/dph/fpp and click on “Food Protection Program regulations”. Then under Food Processing click “105 CMR 500.000: Good Manufacturing Practices for Food”.

This inspection report is signed and certified under the pains and penalties of perjury.

Sincerely,

Amy Medeiros														Environmental Health Inspector, CSP, BCEH