The Commonwealth of Massachusetts

Executive Office of Health and Human Services

Department of Public Health

Bureau of Environmental Health

Community Sanitation Program

5 Randolph Street

Canton, MA 02021

Telephone: 781-828-7910

Facsimile: 781-828-7703

lauren.molotnikov@state.ma.us

DEVAL L. PATRICK GOVERNOR TIMOTHY P. MURRAY LIEUTENANT GOVERNOR JUDYANN BIGBY, MD SECRETARY JOHN AUERBACH COMMISSIONER

May 26, 2010

James V. DiPaola, Sheriff

Middlesex County Jail

40 Thorndike Street

Cambridge, MA 02141

Re: Facility Inspection

Dear Sheriff DiPaola:

In accordance with M.G.L. c. 111, §§ 5, 20, and 21, and Department of Public Health Regulations 105 CMR 451.000: Minimum Health and Sanitation Standards and Inspection Procedures for Correctional Facilities; 105 CMR 480.000: Storage and Disposal of Infectious or Physically Dangerous Medical or Biological Waste (State Sanitary Code, Chapter VIII); 105 CMR 590.000: Minimum Sanitation Standards for Food Establishments (State Sanitary Code Chapter X); the 1999 Food Code; and 105 CMR 205.000 Minimum Standards Governing Medical Records and the Conduct of Physical Examinations in Correctional Facilities; I conducted an inspection of Middlesex County Jail on May 25, 2010 accompanied by Captain William Buckley. Violations noted are listed below (* indicates conditions documented on previous inspection reports).

Lobby

105 CMR 451.350*	Structural Maintenance: Ceiling damaged

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty

Administration Area

Officers 17-12

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light 	fixture not functioning properly

105 CMR 451.350*	Structural Maintenance: Floor tiles missing

105 CMR 451.353*	Interior Maintenance: Several light shields missing

Weight Room

105 CMR 451.344*	Illumination in Habitable Areas: Several bulbs missing and light fixtures not 	functioning properly

105 CMR 451.353*	Interior Maintenance: Light shields missing

105 CMR 451.353	Interior Maintenance: Loose, uncapped wires hanging from light fixture

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty

Male Officer’s Locker Room

105 CMR 451.353*	Interior Maintenance: Vents dirty

105 CMR 451.353*	Interior Maintenance: Vent covers rusted

105 CMR 451.353*	Interior Maintenance: Several light shields missing

105 CMR 451.344	Illumination in Habitable Areas: Two light fixtures not functioning properly

Female Officer’s Locker Room

105 CMR 451.350	Structural Maintenance: Ceiling tiles damaged

105 CMR 451.353	Interior Maintenance: One light shield missing

Officer’s Bathroom

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No paper towels at handwash sink

105 CMR 451.123*	Maintenance: Light shield missing

105 CMR 451.123	Maintenance: Ceiling vent dirty

Sheriff’s Office Area

Female Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling vents dirty

105 CMR 451.123*	Maintenance: Cold water controls difficult to utilize on both sinks

105 CMR 451.123*	Maintenance: Hot water control difficult to utilize on right sink

Slop Sink Room

105 CMR 451.353	Interior Maintenance: Unlabeled chemical bottle

Male Staff Bathroom

No Violations Noted

Kitchenette

FC 4-204.112(A)*	Design and Construction, Functionality: No functioning thermometer in refrigerator

17th Floor Jail Area

Control Area

105 CMR 451.344	Illumination in Habitable Areas: One light fixture not functioning properly

Control Bathroom

105 CMR 451.123*	Maintenance: Sink fixture damaged

Visiting Rooms

No Violations Noted

Deputies Office

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, disposal not functioning properly

Deputies’ Bathroom

No Violations Noted

Holding Cell # 137

No Violations Noted

Bathroom Area	Not in use at the time of inspection

Receiving Area

Common Area

105 CMR 451.345*	Illumination in Common Passage Ways and Areas: Inadequate lighting, several light 	fixtures not functioning properly

105 CMR 451.350	Structural Maintenance: Vent cover damaged

105 CMR 451.350	Structural Maintenance: Ceiling tiles damaged

FC 3-305.11(A)(2)	Preventing Contamination from Premises: Food exposed to dust, fans in cooler dirty

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 560F

FC 4-501.11(A)*	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, kick plate missing from refrigerator unit

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, gasket damaged

FC 4-601.11(A)*	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, possible 	mold growth on the interior surfaces of the refrigerator unit

Holding Tanks

105 CMR 451.117	Toilet Fixtures: Toilet fixture not easily cleanable, toilet paint damaged in left holding 	tank

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, vents painted over in both holding tanks

105 CMR 451.353	Interior Maintenance: Ceiling dirty in both holding tanks

Shower Area	Not in use at the time of inspection

105 CMR 451.123*	Maintenance: Ceiling vent rusted

Laundry

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation, laundry dryer not properly vented to the 	exterior of the building

Staff Bathroom

105 CMR 451.123	Maintenance: Faucet loose

105 CMR 451.123	Maintenance: Light shield missing

Receiving Office

105 CMR 451.344	Illumination in Habitable Areas: One light fixture not functioning properly

105 CMR 451.350	Structural Maintenance: Ceiling tiles loose and damaged

18th Floor

Hallway

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light 	fixture not functioning properly

Caseworker’s Offices

No Violations Noted

Laundry Room	Lock at the time of inspection

18th Floor Cell Block

Control Area

105 CMR 451.344	Illumination in Habitable Areas: Inadequate lighting, one light fixture not functioning	properly

105 CMR 451.353	Interior Maintenance: Vent blocked

Control Bathroom

105 CMR 451.123*	Maintenance: Ceiling tiles missing and damaged

105 CMR 451.123	Maintenance: Light shield missing

105 CMR 451.123	Maintenance: Floor not easily cleanable, floor paint damaged

Laundry Room

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, laundry dryer not vented properly to the 	exterior of the building

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, light fixture 	not functioning properly

A Side

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.320*	Cell Size: Cell block overcrowded, inmates sleeping on boat beds in the common area

105 CMR 451.353	Interior Maintenance: Several light fixtures dirty

105 CMR 451.350	Structural Maintenance: Ceiling damaged near sprinkler head

A Side Shower

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 13 plus inmates

105 CMR 451.123*	Maintenance: Ceiling rusted and paint blistering

105 CMR 451.123*	Maintenance: Light fixture not functioning

105 CMR 451.123	Maintenance: Floor drain cover missing

105 CMR 451.123	Maintenance: Floor damaged outside shower stall

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1180F

B Side

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.344*	Illumination in Habitable Areas: Several light fixtures not functioning properly

105 CMR 451.350	Structural Maintenance: Ceiling damaged

105 CMR 451.353	Interior Maintenance: Vent covers not secured properly across from cell # 10

B Side Shower

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 20 plus inmates

105 CMR 451.123*	Maintenance: Ceiling rusted and paint blistering

105 CMR 451.123*	Maintenance: Floor drain cover missing

105 CMR 451.123	Maintenance: Light fixture not functioning

105 CMR 451.123	Maintenance: Standing water on the floor outside shower unit

105 CMR 451.123	Maintenance: Soap scum on shower floor and curtain

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1200F

C Side

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.353	Interior Maintenance: Vents dirty

C Side Shower

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 20 plus inmates

105 CMR 451.123*	Maintenance: Ceiling rusted and paint blistering

105 CMR 451.123*	Maintenance: Light fixture rusted

105 CMR 451.123*	Maintenance: Floor drain cover missing

105 CMR 451.123	Maintenance: Light fixture not functioning

105 CMR 451.123	Maintenance: Shower floor finish rust stained

105 CMR 451.123	Maintenance: Floor finish damaged outside shower stall

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1150F

D Side

105 CMR 451.103	Mattresses: Mattress damage on overflow bed near cell # 7

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation, vent covers painted over

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.353*	Interior Maintenance: Vent covers dirty

105 CMR 451.353	Interior Maintenance: Portable fan dirty

105 CMR 451.353	Interior Maintenance: Several light fixtures dirty

D Side Shower

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 20 plus inmates

105 CMR 451.123*	Maintenance: Ceiling rusted and paint blistering

105 CMR 451.123	Maintenance: Light fixture not functioning

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1150F

Max Cell Block

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation, vents blocked

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.350*	Structural Maintenance: Ceiling damaged

18th Floor Dorm

Control Area

105 CMR 451.344	Illumination in Habitable Areas: One light fixture not functioning properly

105 CMR 451.353	Interior Maintenance: Counter top not easily cleanable, surface damaged

Control Bathroom

105 CMR 451.123	Maintenance: Ceiling tiles damaged

105 CMR 451.123	Maintenance: Light shield missing

105 CMR 451.123	Maintenance: Unlabeled chemical bottle

Inmate Bathroom

105 CMR 451.123*	Maintenance: Plastic bar cover damaged

105 CMR 451.123	Maintenance: Floor not easily cleanable, paint and floor damaged

105 CMR 451.123	Maintenance: Electrical hand dryers not functioning properly

105 CMR 451.123	Maintenance: Floor dirty

105 CMR 451.123	Maintenance: Vent damaged and dirty in toilet area

Shower Area

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 functioning shower for 60 	plus inmates

105 CMR 451.123*	Maintenance: Shower water controls missing in right shower stall

105 CMR 451.123*	Maintenance: Drain cover missing in left shower stall

105 CMR 451.123*	Maintenance: Ceiling rusted in shower area

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, right shower stall out of order

Laundry

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, laundry dryer not vented properly to the 	exterior of the building

Janitor’s Closet

105 CMR 451.353*	Interior Maintenance: Ceiling wet and water stained near smoke detector

105 CMR 451.353	Interior Maintenance: Unlabeled chemical bottle

105 CMR 451.353	Interior Maintenance: Door and door frame paint damaged

Dorm Room

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor tiles damaged

105 CMR 451.350	Structural Maintenance: Ceiling damaged and water stained

105 CMR 451.353	Interior Maintenance: Wall paint damaged

Day Room

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room, several inmates sleeping in day room

105 CMR 451.350*	Structural Maintenance: Floor tiles damaged

105 CMR 451.353	Interior Maintenance: Vent dirty

105 CMR 451.353	Interior Maintenance: Floor dirty

105 CMR 451.353	Interior Maintenance: Window sills dirty

19th Floor

19th Floor Cell Block

Control Area

105 CMR 451.345*	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light 	fixture not functioning properly

Control Bathroom

105 CMR 451.123*	Maintenance: Vent cover not properly secured and dirty

105 CMR 451.123	Maintenance: Sink fixture not secured properly to wall

Laundry Room

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, laundry dryer not vented to the exterior 	of the building

Mop Closet

105 CMR 451.353	Interior Maintenance: Mop not allowed to dry properly, wet mop left on floor

E Side

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.344	Illumination in Habitable Areas: One light fixture not functioning properly

105 CMR 451.353	Interior Maintenance: Vent dirty

E Side Shower

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 20 plus inmates

105 CMR 451.123*	Maintenance: Ceiling rusted and paint blistering

105 CMR 451.123*	Maintenance: Floor drain cover missing

105 CMR 451.123	Maintenance: Light fixture not functioning

F Side

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation, several vents painted over

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.353*	Interior Maintenance: Several vents dirty

105 CMR 451.353	Interior Maintenance: Portable fan dirty

F Side Shower

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 15 plus inmates

105 CMR 451.123	Maintenance: Soap scum on walls in shower stall

105 CMR 451.123	Maintenance: Caulking around metal plate dirty

105 CMR 451.123	Maintenance: Ceiling rusted and paint blistering

G Side

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.353	Interior Maintenance: Outlet cover loose on ceiling across from cell # 8

105 CMR 451.353	Interior Maintenance: Light cover loose across from cell # 10

105 CMR 451.353	Interior Maintenance: Light fixture dirty

G Side Shower	Occupied at the time of inspection

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 20 plus inmates

H Side

105 CMR 451.117*	Toilet Fixtures: Toilet fixtures not easily cleanable, old toilet paint damaged

105 CMR 451.141*	Screens: Several window screens missing

105 CMR 451.320*	Cell Size: Inadequate floor space in cell block, inmates sleeping in the common area

105 CMR 451.344*	Illumination in Habitable Areas: Several light fixtures not functioning properly

105 CMR 451.353	Interior Maintenance: Light fixtures dirty

105 CMR 451.353	Interior Maintenance: Vent covers dirty

H Side Shower

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 20 plus inmates

105 CMR 451.123*	Maintenance: Ceiling rusted and paint blistering

105 CMR 451.123*	Maintenance: Standing water on the floor outside shower unit

105 CMR 451.123*	Maintenance: Floor drain cover missing

105 CMR 451.123	Maintenance: Floor finish damaged outside shower unit

Food Service Area

Dinning Room

FC 6-501.11*	Maintenance and Operation; Repairing: Facility not in good repair, ceiling water 	damaged

Kitchen

FC 6-201.11	Design, Construction and Installation: Floor not easily cleanable, floor finish damaged 	throughout kitchen

Service Line

FC 4-202.16	Design and Construction, Nonfood-Contact Surfaces: Nonfood-contact surfaces not 	designed and constructed to allow easy cleaning and maintenance, cloth used to secure 	the waste tub on drink dispenser

3-Compartment Sink

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, pipe leaking from wash compartment

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, several facets leaking on 3 compartment sink

Steam Table

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, faucet loose on handwashing sink

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, faucet leaking on handwash sink

Kettle and Stove Hood Area

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, two light fixtures 	not functioning properly

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, insulation 	damaged on old steam pipe

Dish Room

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, sprinkler heads 	coated in dust

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, light shield loose

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, insulation on 	pipes dirty

Refrigerator # 4

FC 3-305.11(A)(2)	Preventing Contamination from Premises: Food exposed to dust, fans in cooler dirty

Refrigerator # 5

FC 4-501.11(A)*	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, gasket damaged

Prep Table Area and 2 Compartment Sink

FC 4-601.11(A)	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, can 	opener dirty

FC 5-205.15(B)*	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, faucets leaking on 2 compartment sink

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, several light 	fixtures not functioning properly

Pots and Pans Cage

No Violations Noted

Refrigerator # 1

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 520F

FC 6-501.11*	Maintenance and Operation; Repairing: Facility not in good repair, floor drain 	clogged outside refrigerator unit

Freezer # 3

FC 4-501.11(A)*	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, ceiling damaged

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, ice building up observed on ceiling

Inmate Bathroom

FC 5-202.12(A)	Plumbing System, Design: Handwashing sinks water temperature recorded at 1450F

FC 6-202.14	Design, Construction, and Installation; Functionality: Toilet room not completely 	enclosed, door left open and self-closer not functioning properly

Staff Bathroom

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, hot water not functioning properly

Staff Office

FC 3-501.16(B)*	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 460F

FC 4-602.12(B)*	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, one light fixture 	not functioning properly

Knife Storage Room

No Violations Noted

Empty Can Bin

FC 6-501.111(B)	Maintenance and Operations; Pest Control: A swarm of flying insects observed in and 	around empty cans

Dry Storage Room

No Violations Noted

Refrigerator # 2

FC 3-305.11(A)(1)	Preventing Contamination from Premises: Food stored in an inappropriate location, 	food stored under leaking condenser unit

FC 4-501.11(A)*	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, condenser unit spitting water on the ceiling, walls, and floor in refrigerator unit

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, paint peeling from condenser unit

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface not 	maintained properly, standing water observed on floor in refrigerator unit

Back Area

FC 6-501.11*	Maintenance and Operation; Repairing: Facility not in good repair, unfilled hole in 	window from old air conditioner vent

FC 6-501.11*	Maintenance and Operation; Repairing: Facility not in good repair, ceiling damaged

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, light shield not 	installed properly

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, window sills 	dirty

Ice Machines

FC 4-502.11(A)	Maintenance and Operation, Utensils: Utensils not maintained in a state of good	repair, ice scoop holders dirty and damaged in both machines

FC 4-601.11(A)	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, interior 	surfaces of ice machine dirty in machine # 1

Food Service Manager’s Office

FC 3-701.11(D)	Contaminated Food, Disposition: Ready-to-eat food contaminated by employees not 	properly discarded, sugar contaminate with coffee grinds

20th Floor

Hallway

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

Medical Area

105 CMR 451.353	Interior Maintenance: Ceiling water damaged

Staff Bathroom

105 CMR 451.123	Maintenance: Ceiling water damaged

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1060F

Medical Staff Kitchenette

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet leaking

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, gasket dirty and damaged

Exam Room

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet loose

Medical Cells

105 CMR 451.218(A)	Windows to Outdoors in New and Renovated Facilities: No window providing natural 	light within medical cell # 1, 2, and 3

Special Management Unit

105 CMR 451.103*	Mattresses: Mattress damage in bed # 39

105 CMR 451.141*	Screens: Screens missing

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Ceiling tiles damaged and rusted

Control Area

105 CMR 451.350	Structural Maintenance: Counter top not easily cleanable, cover missing and damaged

Laundry

105 CMR 451.140	Adequate Ventilation: Inadequate ventilation, laundry dryer not vented properly

Bathroom

105 CMR 451.123*	Maintenance: Ceiling water damaged

105 CMR 451.123	Maintenance: Floor not easily cleanable, floor paint damaged

105 CMR 451.123	Maintenance: Standing water observed on bathroom floor

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 670F

Shower Stall	Occupied at the time of inspection

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 40 plus inmates

Day Room

105 CMR 451.350*	Structural Maintenance: Ceiling tiles damaged

Slop Sink Room

105 CMR 451.353	Interior Maintenance: Unlabeled chemical bottle

20 Rear Cells

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 3

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, cell # 3 out of order at the time of 	inspection

105 CMR 451.141	Screens: One screen missing in hallway

105 CMR 451.218(A)	Windows to Outdoors in New and Renovated Facilities: No window providing natural 	light within cells

105 CMR 451.350	Structural Maintenance: Wall damaged in cell # 2

Shower Stall

105 CMR 451.119*	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 40 plus inmates

105 CMR 451.123	Maintenance: Standing water observed on floor outside shower unit

105 CMR 451.123	Maintenance: Shower curtain dirty

105 CMR 451.123	Maintenance: Floor drain cover missing

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head leaking

20th Floor Overflow Dorm

105 CMR 451.322	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

105 CMR 451.353	Interior Maintenance: Ceiling tiles not installed properly

Bathroom

105 CMR 451.114*	Shared Toilet and Handwashing Facilities: Inadequate number of toilet facilities	handwash sinks per inmate population, 2 sinks and 2 toilets for 30 plus inmates

105 CMR 451.123*	Maintenance: Floor not easily cleanable, floor damaged

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, hot water not working at sink # 2

Administrative Segregation

105 CMR 451.141*	Screens: Screens missing

105 CMR 451.345*	Illumination in Common Passage Ways and Areas: Inadequate lighting, several light 	fixtures not functioning properly

105 CMR 451.353	Interior Maintenance: Vent cover missing

Cells

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not functioning properly in cell # 6

105 CMR 451.350	Structural Maintenance: Wall paint damaged in cell # 4

Shower Stall	Occupied at the time of inspection

105 CMR 451.119	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 40 plus inmates

OV3 Annex

105 CMR 451.141*	Screens: Several screens missing

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Ceiling tiles damaged and missing

105 CMR 451.350*	Structural Maintenance: Floor tiles damaged

105 CMR 451.350*	Structural Maintenance: Light shield not installed properly

105 CMR 451.353	Interior Maintenance: Vent dirty

105 CMR 451.353	Interior Maintenance: Wall not easily cleanable, wall paint damaged

Bathroom

105 CMR 451.114*	Shared Toilet and Handwashing Facilities: Inadequate number of toilet facilities and 	handwash sinks per inmate population, 1 toilet and sink fixture for 45 inmates

105 CMR 451.123*	Maintenance: Floor tiles damaged

105 CMR 451.123*	Maintenance: Handwash sink dirty

105 CMR 451.123*	Maintenance: Unlabeled chemical bottle

105 CMR 451.123	Maintenance: Metal access panel rusted

Hallway Shower Room

105 CMR 451.119	Bathing Facilities: Inadequate shower to inmate ratio, 1 shower for 45 plus inmates

105 CMR 451.123*	Maintenance: Standing water observed on floor outside shower unit

105 CMR 451.123*	Maintenance: Vent cover missing

105 CMR 451.123	Maintenance: Cloth shower curtain wet with possible mold growth

105 CMR 451.123	Maintenance: Floor not easily cleanable, floor paint damaged

105 CMR 451.123	Maintenance: Shower wall damaged

Stairway # 2

105 CMR 451.350	Structural Maintenance: Ceiling tiles loose and damaged

105 CMR 451.353	Interior Maintenance: Ceiling tiles water stained

Recreational Decks

No Violations Noted

Observations and Recommendations

- Eyewash sink not maintained in medical exam room, recommend cleaning and recapping eyewash sink

- There is an inadequate number of showers, toilets, and handwash sinks throughout the facility

- Please provided documentation confirming that all blankets supplied to inmates are fire retardant in accordance with 105 CMR 451.101

This facility does not comply with the Department’s Regulations cited above. In accordance with 105 CMR 451.404, please indicate next to each entry on the inspection report a plan of correction. Said plan of correction must be submitted within 10 days of receipt of this letter and should detail the specific steps that will be taken and the date of expected compliance. The plan of correction should be submitted to my attention, at the address listed above.

To review the specific regulatory requirements please visit our website at www.mass.gov/dph/dcs and click on "Community Sanitation Regulations" (available in both PDF and RTF formats).

To review the Food Establishment regulations please visit the Food Protection website at www.mass.gov/dph/fpp and click on “Food Protection Regulations”. Then under “Retail” click “105 CMR 590.000 - State Sanitary Code Chapter X – Minimum Sanitation Standards for Food Establishments” and “1999 Food Code”.

This inspection report is signed and certified under the pains and penalties of perjury.

Sincerely,

Lauren Molotnikov

Environmental Health Inspector, CSP, BEH

cc:	Suzanne K. Condon, Associate Commissioner, Director, BEH

Steven Hughes, Director, CSP, BEH

JudyAnn Bigby, MD, Secretary, Executive Office of Health and Human Services

Harold W. Clarke, Commissioner, DOC

Scott Brazis, Superintendent

Cambridge Inspectional Services

Captain William Buckley, Safety & Communications Officer

Clerk, Massachusetts House of Representatives

Clerk, Massachusetts Senate

Mary Elizabeth Heffernan, EOPS