The Commonwealth of Massachusetts

Executive Office of Health and Human Services

Department of Public Health

Bureau of Environmental Health

Community Sanitation Program

5 Randolph Street

Canton, MA 02021

Telephone: 781-828-7910

Facsimile: 781-828-7703

lauren.molotnikov@state.ma.us

DEVAL L. PATRICK GOVERNOR TIMOTHY P. MURRAY LIEUTENANT GOVERNOR JUDYANN BIGBY, MD SECRETARY JOHN AUERBACH COMMISSIONER

May 13, 2010

Bruce Gelb, Superintendent

MCI Concord

965 Elm Street

P.O. Box 9106

Concord, MA 01742

Re: Facility Inspection

Dear Superintendent Gelb:

In accordance with M.G.L. c. 111, §§ 5, 20, and 21, and Department of Public Health Regulations 105 CMR 451.000: Minimum Health and Sanitation Standards and Inspection Procedures for Correctional Facilities; 105 CMR 480.000: Storage and Disposal of Infectious or Physically Dangerous Medical or Biological Waste (State Sanitary Code, Chapter VIII); 105 CMR 590.000: Minimum Sanitation Standards for Food Establishments (State Sanitary Code Chapter X); the 1999 Food Code; and 105 CMR 205.000 Minimum Standards Governing Medical Records and the Conduct of Physical Examinations in Correctional Facilities; I conducted an inspection of MCI Concord on May 11 and 12, 2010 accompanied by Sergeant George Frascarelli, EHSO and Cornelius Jones, EHSO. Violations noted are listed below (* indicates conditions documented on previous inspection reports).

Building A

Lobby

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty

Women’s Bathroom

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1500F

Men’s Bathroom

105 CMR 451.123*	Maintenance: Wall and floor tiles damaged

105 CMR 451.123	Maintenance: Floor drain cover not secured properly

105 CMR 451.123	Maintenance: Screen damaged and not installed properly

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1600F

Administration Area

Women’s Bathroom

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1500F

Men’s Room

105 CMR 451.117	Toilet Fixtures: Urinal dirty

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1400F

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, faucet not secured properly on 	sink # 2

Janitor’s Closet

105 CMR 451.353	Interior Maintenance: Light shield not provided in a maintenance area

Water Fountain

No Violations Noted

Coffee Station

No Violations Noted

Holding Tank

Cell A

No Violations Noted

Cell B

No Violations Noted

Building B

Old Staff Lounge

Male Staff Bathroom

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 750F

Female Staff Bathroom

105 CMR 451.123*	Maintenance: Wall tiles damaged

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 730F

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, hot water handle leaking

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet leaking

Storage Closet

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, light not 	functioning properly

Kitchenette Area/Break Room

105 CMR 451.344	Illumination in Habitable Areas: Three light fixtures not working properly

105 CMR 451.353*	Interior Maintenance: Ceiling tiles and paint damaged

105 CMR 451.353	Interior Maintenance: Screen damaged

Weight Room

105 CMR 451.353*	Interior Maintenance: Ceiling tiles and paint damaged

Visiting Room

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, excess water pressure at water 	fountain

105 CMR 451.353*	Interior Maintenance: Vent cover missing

Back Room

105 CMR 451.353	Interior Maintenance: Window shades damaged

105 CMR 451.353	Interior Maintenance: Wall and wall paint damaged

105 CMR 451.353	Interior Maintenance: Baseboard missing

Treasurer’s Office Area

Inmate Bathroom (Urinalysis Bathroom)

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 740F

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet leaking

Treasurer’s Bathroom

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 770F

Treasurer’s Kitchenette

No Violations Noted

B corridor

Inmate Bathroom

105 CMR 451.123*	Maintenance: Wall vent rusted

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 750F

Vending Machines

No Violations Noted

B Corridor Slop Sink Room

105 CMR 451.353*	Interior Maintenance: Light shield not provided in a maintenance area

Male Staff Bathroom

105 CMR 451.123*	Maintenance: Vent rusted in toilet stall # 2

105 CMR 451.123*	Maintenance: Wall tiles missing in toilet stall # 2

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 710F

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, sink # 2 out of order

Water Fountain

No Violations Noted

Female Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling damaged

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 730F

B Building Control

105 CMR 451.353	Interior Maintenance: Vent cover missing

105 CMR 451.123	Maintenance: Light covers missing

B Control Bathroom

105 CMR 451.123	Maintenance: Wall vent dirty

105 CMR 451.123	Maintenance: Wall grout missing in corners

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1650F

B Control Kitchenette

No Violations Noted

C Building

CRA Program

First Floor Control

No Violations Noted

Staff Bathroom

105 CMR 451.123	Maintenance: Light shield missing

105 CMR 451.126	Hot Water: Hot water temperature recorded at 670F

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet not secured properly

Storage Room

No Violations Noted

Slop Sink Room

No Violations Noted

First Floor Shower # 1

105 CMR 451.123*	Maintenance: Ceiling vent dirty

105 CMR 451.123*	Maintenance: Standing water observed on shower floor

105 CMR 451.123	Maintenance: Ceiling dirty

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.130	Hot Water: No hot water provided to the shower unit at the time of inspection

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, shower head # 2 leaking

First Floor Shower # 2

105 CMR 451.123*	Maintenance: Shower wall cover damaged

105 CMR 451.123*	Maintenance: Floor tiles damaged

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Wall cover not sealed to floor properly

105 CMR 451.130	Hot Water: No hot water provided to the shower unit at the time of inspection

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 14

105 CMR 451.103	Mattresses: Mattress damage in cell # 20

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 1, 2, 3, 4, 22, and 24

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 2, 4, 5, 6, 9, 15, 17, 19, 22, and 23

TV Room

105 CMR 451.350	Structural Maintenance: Floor tiles and baseboard damaged

105 CMR 451.350	Structural Maintenance: Window pane damaged

Second Floor Control

105 CMR 451.350*	Structural Maintenance: Window pane damaged

105 CMR 451.350	Structural Maintenance: Ceiling damage not repaired in a workman like manner

Staff Bathroom

105 CMR 451.123	Maintenance: Light shield missing

105 CMR 451.123	Maintenance: Wall tile grout missing in corners

105 CMR 451.123	Maintenance: Ceiling vent dirty

Slop Sink Room

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, hot water handle leaking

Second Floor Shower # 1

105 CMR 451.123	Maintenance: Floor tiles missing and damaged

105 CMR 451.123	Maintenance: Wall tiles missing and damaged

105 CMR 451.123	Maintenance: Vent cover rusted

105 CMR 451.123	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Paint damaged on door frame

105 CMR 451.130	Hot Water: No hot water provided to the shower unit at the time of inspection

Second Floor Shower # 2

105 CMR 451.123	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Flying insects observed in shower area

105 CMR 451.123	Maintenance: Paint peeling and metal rusted on wall

105 CMR 451.123	Maintenance: Soap scum on walls in shower and shower curtain

105 CMR 451.123	Maintenance: Shower curtain damaged

105 CMR 451.130	Hot Water: No hot water provided to the shower unit at the time of inspection

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 32

105 CMR 451.350	Structural Maintenance: Window pane missing in cell # 34

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 26, 27, 28, 32, 36, 37, 38, 43, 44, 	and 49

TV Room

105 CMR 451.141	Screens: Screen damaged

CRA Program Basement

Inmate Bathroom

105 CMR 451.123	Maintenance: Light shield missing

Classrooms

No Violations Noted

Stairway

105 CMR 451.350	Structural Maintenance: Floor tiles missing

SMU-First Floor

Medical Exam Room C1-10

105 CMR 451.353	Interior Maintenance: Vent dirty

Staff Bathroom C1-11

No Violations Noted

Slop Sink Room C1-62

105 CMR 451.350	Structural Maintenance: Ceiling damaged

Showers

105 CMR 451.123	Maintenance: Soap scum on walls and floor in shower # C1-60 and C1-61

105 CMR 451.123	Maintenance: Ceiling vent dirty in shower # C1-60 and C1-61

105 CMR 451.123	Maintenance: Soap scum on shower chair in shower # C1-60

Water Fountain

No Violations Noted

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 1-30, 1-33, and 1-49

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 1-34 and 1-58

Staff Break Room C1-22

105 CMR 451.353	Interior Maintenance: Vent dirty

Property C1-23

105 CMR 451.353	Interior Maintenance: Vent dirty

Recreational Decks

No Violations Noted

SMU-Second Floor

Slop Sink Room C2-26

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

105 CMR 451.353	Interior Maintenance: Floor dirty

Showers

105 CMR 451.123	Maintenance: Ceiling vent dirty in shower # C2-60 and C2-61

105 CMR 451.123	Maintenance: Soap scum on walls and floor in shower # C2-60 and C2-61

105 CMR 451.123	Maintenance: Wall damaged in shower # C2-61

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 2-50

105 CMR 451.102	Pillows and Linens: Shirt being used for a pillow case in cell # 2-58

105 CMR 451.103	Mattresses: Mattress damage in cell # 2-31 and 2-54

Showers

105 CMR 451.123	Maintenance: Ceiling vent dirty in shower # C2-24, C2-25, and C2-26

Room C2-22

105 CMR 451.353	Interior Maintenance: Vent dirty

Room C2-23

105 CMR 451.353	Interior Maintenance: Vent dirty

Recreational Deck

No Violations Noted

Building D

Exterior

FC 6-202.15(A)(2)	Design, Construction, and Installation; Functionality: Red exterior door not weather 	and vermin tight

Food Service Area

FC 6-501.11*	Maintenance and Operation; Repairing: Facility not in good repair, floor grout 	damaged in between pots and pans room and dry storage room

Barrel Wash Room

No Violations Noted

B Tool Room #1 (1377)

No Violations Noted

Milk Refrigerator # 1376

FC 3-305.11(A)(2)	Preventing Contamination from Premises: Food exposed to dust, fans in cooler dusty

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 41 to 480F, temperature not stable within refrigerator unit

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, floor damaged

FC 6-202.11(A)	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

Bread Storage Room

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, window sill dirty

Freezer

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, shelves not secured properly

Staff Office

FC 3-302.11(A)(4)	Preventing Food and Ingredient Contamination: Preventing cross contamination, food 	not appropriately covered, bag of salt left open

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, refrigerator gasket damaged

Staff Bathroom

FC 5-202.12(A)	Plumbing System, Design: Handwashing sinks water temperature recorded at 1350F

B Tool Room # 2

FC 6-202.11(A)	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, unfinished wooden 	shelves wet and rotted making the area not easily cleanable and causing a strong odor

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, standing water 	observed on floor

Inmate Bathroom

FC 5-202.12(A)	Plumbing System, Design: Handwashing sinks water temperature recorded at 1350F

FC 5-205.15(B)*	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, faucet loose

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, vent dirty

Bakery/Dry Storage Room

FC 3-302.11(A)(4)	Preventing Food and Ingredient Contamination: Preventing cross contamination, food 	not appropriately covered, bag of baking soda left open

FC 5-202.12(A)	Plumbing System, Design: Handwashing sinks water temperature recorded at 1450F

FC 6-301.14	Numbers and Capacity; Handwashing Facilities: Handwashing signage not visible

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, ceiling tiles not 	installed properly

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, vent cover missing

Walk-in Freezers

FC 3-305.11(A)(2)	Preventing Contamination from Premises: Food exposed to dust, fans in cooler dusty

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty, wall 	dirty

FC 3-305.11(A)(1)	Preventing Contamination from Premises: Food stored in an inappropriate location, 	food stored under leaking condenser

New Freezers

No Violations Noted

Pots and Pans Room

No Violations Noted

South Side

Kettles and Ovens Hood Area

FC 6-202.11(A)*	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, one light fixture 	not functioning properly above ovens

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, wall damaged

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, ceiling paint 	damaged

Handwash Sink

FC 5-202.12(A)	Plumbing System, Design: Handwashing sinks water temperature recorded at 1400F

Tray Prep

FC 4-202.11(A)(2)	Design and Construction, Cleanability: Damaged food-contact surface no longer	easily cleanable, several damaged trays being used for food service

FC 5-202.12(A)	Plumbing System, Design: Handwashing sinks water temperature recorded at 1400F

Traulsen Cooler

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 500F, gasket not functioning properly

Food Warmers

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, doors latch and gasket damaged

North Side

Hoods

FC 6-202.11(A)*	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, faucet lose on wash sink

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, wall damaged

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor drains not 	functioning properly causing a strong odor

Handwash Sink

No Violations Noted

Traulsen Cooler

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 500F, gasket not functioning properly

Mechanical Warewashing Room

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, faucet leaking

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, vent cover missing

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, ceiling panel 	missing

South Side Dinning Room

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, water dispenser drain not functioning properly

FC 6-202.15(A)(2)	Design, Construction, and Installation; Functionality: Yellow exterior door not 	weather and vermin tight

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, window sills 	dirty

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor grout 	missing in several areas

North Side Dinning Room

FC 5-205.15(B)	Plumbing System, Operations and Maintenance: Plumbing system not maintained in 	good repair, faucet leaking near warmers on food line

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor grout 	missing in several areas

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor damaged 	near doorway

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, window sills 	dirty

Vegetable Box

FC 3-305.11(A)(2)	Preventing Contamination from Premises: Food exposed to dust, fans in cooler dusty

Meat Refrigerator

FC 3-305.11(A)(2)	Preventing Contamination from Premises: Food exposed to dust, fans in cooler dusty

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, shelf not stable

Ice Machine

FC 4-202.11(A)(2)	Design and Construction, Cleanability: Damaged food-contact surface no longer	easily cleanable, ice scoop damaged

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, not functioning properly

FC 4-601.11(A)	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, interior 	surfaces of ice machine dirty

Building E

West Side

Stairway

105 CMR 451.350*	Structural Maintenance: Window pane damaged

West Down Control

105 CMR 451.353	Interior Maintenance: Counter top and drawer covers damaged and no longer easily 	cleanable

Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Wall tiles missing

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1700F

West Down Low

Hallway

105 CMR 451.350	Structural Maintenance: Floor damaged

Showers	Shower occupied at the time of inspection

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 122

105 CMR 451.350	Structural Maintenance: Window not weather tight, pane missing in cell # 125

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 126

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 105, 110, 111, 112, 113, 118, 	123, 124, and 126

Day Room

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light 	fixture not working properly

105 CMR 451.353*	Interior Maintenance: Window sills filled with trash

Phone Room

105 CMR 451.353	Interior Maintenance: Window sills filled with trash

West Down High

Hallway

105 CMR 451.350	Structural Maintenance: Floor damaged

Slop Sink Room

105 CMR 451.353	Interior Maintenance: Light shield damaged

Showers

105 CMR 451.119	Bathing Facilities: Inadequate shower to inmate ratio, 2 shower heads available for 50 	plus inmates

105 CMR 451.123	Maintenance: Shower walls need re-grouting

105 CMR 451.123	Maintenance: Ceiling dirty

105 CMR 451.123	Maintenance: Shower curtain secured by absorbent string

105 CMR 451.123	Maintenance: Dirty tap on upper wall tiles

105 CMR 451.123	Maintenance: Wall tiles damaged

105 CMR 451.123	Maintenance: Soap scum on lower walls in shower

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, 3 shower head unit not 	functioning at the time of inspection

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, 1 shower head missing from 3 	shower head unit

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 129

105 CMR 451.350	Structural Maintenance: Window not weather tight in cell # 138 and 150

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 129 and 141

Day Room

105 CMR 451.353	Interior Maintenance: Window sills filled with trash

West Up Control

105 CMR 451.344	Illumination in Habitable Areas: One light fixture not working properly

105 CMR 451.353	Interior Maintenance: Counter top and drawer covers damaged and no longer easily 	cleanable

Control Closet

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, refrigerator gasket damaged

Staff Bathroom

105 CMR 451.123*	Maintenance: Light shield missing

105 CMR 451.123*	Maintenance: Interior door frame loose from wall

105 CMR 451.123	Maintenance: Sink not properly secured to wall

105 CMR 451.123	Maintenance: Shower walls need re-grouting in some areas

105 CMR 451.123	Maintenance: Wall tiles damaged

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1800F

West Up Low

Hallway

105 CMR 451.350*	Structural Maintenance: Floor damaged

Showers

105 CMR 451.123*	Maintenance: Light fixture dirty

105 CMR 451.123*	Maintenance: Wall tiles damaged

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123	Maintenance: Soap scum on walls in shower

105 CMR 451.123	Maintenance: Shower curtain secured by absorbent string

105 CMR 451.123	Maintenance: Ceiling outside shower unit dirty and paint damaged

105 CMR 451.126	Hot Water: Hot water temperature recorded at 950F

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation in shower area

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 222

105 CMR 451.350	Structural Maintenance: Window pane missing in cell # 204 and 215

105 CMR 451.350	Structural Maintenance: Window pane damaged in cell # 210

Day Room

105 CMR 451.353	Interior Maintenance: Window sills filled with trash

Phone Room

105 CMR 451.353	Interior Maintenance: Window sills filled with trash

West Up High

Hallway

105 CMR 451.350*	Structural Maintenance: Floor damaged

Broom Closet

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly

105 CMR 451.350*	Structural Maintenance: Window pane damaged

105 CMR 451.350	Structural Maintenance: Floor damaged

105 CMR 451.353*	Interior Maintenance: Ceiling paint damaged

105 CMR 451.353*	Interior Maintenance: Wall paint damaged

Slop Sink Room

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, water control handle leaking

105 CMR 451.353	Interior Maintenance: Wall rusted and no longer easily cleanable

Showers

105 CMR 451.123*	Maintenance: Shower walls need re-grouting

105 CMR 451.123*	Maintenance: Wall tiles damaged

105 CMR 451.123	Maintenance: Soap scum on walls in shower

105 CMR 451.123	Maintenance: Shower curtain secured by absorbent string

105 CMR 451.123	Maintenance: Vent damaged

105 CMR 451.123	Maintenance: Vent dirty

105 CMR 451.124	Water Supply: Insufficient water supply in quantity and pressure, 3 shower head unit 	runs for a few seconds

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation in shower area

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 239 and 242

105 CMR 451.350	Structural Maintenance: Window pane missing in cell # 229, 232, and 238

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 248

Day Room

105 CMR 451.353	Interior Maintenance: Window sills filled with trash

105 CMR 451.353	Interior Maintenance: Window paint damaged

East Side

Stairway

105 CMR 451.350	Structural Maintenance: Window pane damaged

East Down Control

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 500F

105 CMR 451.353	Interior Maintenance: Counter top and drawer covers damaged and no longer easily 	cleanable

Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling and ceiling paint damaged

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1370F

East Down Low

Hallway

105 CMR 451.350	Structural Maintenance: Floor damaged

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged

Showers

105 CMR 451.119	Bathing Facilities: Inadequate shower to inmate ratio, 2 shower heads available for 50 	plus inmates

105 CMR 451.123*	Maintenance: Wall tiles damaged

105 CMR 451.123*	Maintenance: Pipe on ceiling and vent cover rusted

105 CMR 451.123*	Maintenance: Floor tiles damaged and missing

105 CMR 451.123	Maintenance: Shower curtain secured by absorbent string

105 CMR 451.123	Maintenance: Ceiling rusted outside shower unit

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, 3 shower head unit not 	functioning at the time of inspection

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation in shower area

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 317

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 302, 303, 309, 310, 311, 312, 	314, 318, 319, 322, 323, 325, and 327

Day Room

105 CMR 451.350	Structural Maintenance: Floor damaged

Phone Room

105 CMR 451.350	Structural Maintenance: Wall damaged

East Down High

Hallway

105 CMR 451.350*	Structural Maintenance: Floor damaged

Slop Sink Room

105 CMR 451.130	Plumbing: Backflow preventer cap missing on slop sink

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet not secured properly

Showers

105 CMR 451.123*	Maintenance: Wall tiles damaged

105 CMR 451.123*	Maintenance: Shower walls and floor need re-grouting

105 CMR 451.123*	Maintenance: Vent rusted

105 CMR 451.123	Maintenance: Shower curtain secured by absorbent string

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation in shower area

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 337 and 350

105 CMR 451.350	Structural Maintenance: Window pane missing in cell # 329, 333, 336, and 347

105 CMR 451.353	Interior Maintenance: Ceiling rusted above toilet units in cell # 341 and 344

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 328, 330, 331, 333, 339, 344, 	346, 348, 352, and 353

Day Room

No Violations Noted

East Up Control

105 CMR 451.353	Interior Maintenance: Counter top and drawer covers damaged and no longer easily 	cleanable

Staff Bathroom

105 CMR 451.123*	Maintenance: Window sill dirty

105 CMR 451.123	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Insects observed in bathroom

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1330F

East Up Low

Hallway

105 CMR 451.350	Structural Maintenance: Floor damaged

Showers

105 CMR 451.123*	Maintenance: Ceiling, wall, floor, and step tiles missing and damaged

105 CMR 451.123	Maintenance: Light fixture dirty

105 CMR 451.123	Maintenance: Ceiling paint damaged outside shower unit

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation in shower area

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 411

105 CMR 451.126	Hot Water: Hot water temperature recorded at 660F in cell # 443

105 CMR 451.350	Structural Maintenance: Window pane missing in cell # 431, 432, 444, and 452

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 413

105 CMR 451.353	Interior Maintenance: Window sill filled with trash in cell # 414 and 424

Day Room

105 CMR 451.353*	Interior Maintenance: Window sills filled with trash

Phone Room

No Violations Noted

East Up High

Hallway

105 CMR 451.350	Structural Maintenance: Floor damaged

Broom Closet

105 CMR 451.350	Structural Maintenance: Window pane damaged

105 CMR 451.353	Interior Maintenance: Wall paint damaged

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged

105 CMR 451.353	Interior Maintenance: Light shield not provided in a maintenance area

Slop Sink Room

105 CMR 451.130*	Plumbing: Backflow preventer cap missing on slop sink

Showers

105 CMR 451.123*	Maintenance: Wall and floor tiles damaged

105 CMR 451.123*	Maintenance: Shower ceiling, walls, and floor need re-grouting

105 CMR 451.123	Maintenance: Vent dirty

105 CMR 451.123	Maintenance: Light fixture rusted

105 CMR 451.123	Maintenance: Step tiles missing

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation in shower area

Cells

No Violations Noted

Day Room

105 CMR 451.353*	Interior Maintenance: Window sills filled with trash

Building H

Basement

H-1 Overflow Housing Unit	Closed

Workout Room

No Violations Noted

Inmate Bathroom

105 CMR 451.123*	Maintenance: Floor dirty

Stairway

105 CMR 451.350	Structural Maintenance: Floor tiles damaged and missing

First Floor

Hallway

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light 	fixture not working properly

105 CMR 451.350*	Structural Maintenance: Wall damaged

Gym Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123*	Maintenance: Floor tiles damage near doorway

Gym

No Violations Noted

Office

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, refrigerator gasket damaged

Staff Bathroom

105 CMR 451.123	Maintenance: Wall damaged

Inmate Bathroom

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No soap at handwash sink

105 CMR 451.123	Maintenance: Ceiling paint damaged

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, no water provided to sink # 3

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, water running in sink # 2

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, urinal running

Slop Sink Room

105 CMR 451.353	Interior Maintenance: Slop sink not easily cleanable

105 CMR 451.353	Interior Maintenance: Uncapped wires on ceiling

Barber Shop

105 CMR 451.353*	Interior Maintenance: Insulation not secured properly to vent

105 CMR 451.353	Interior Maintenance: Ceiling panels not installed properly

Second Floor

Hallway

No Violations Noted

Inmate Bathroom

105 CMR 451.123	Maintenance: Wall damaged

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, tile #2 out of order

Male Staff Bathroom

105 CMR 451.123*	Maintenance: Light shield damaged

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1330F

Female Staff Bathroom

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1330F

Slop Sink Room

No Violations Noted

Building I

Staff Office

FC 4-501.11(A)*	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, freezer controls missing

Front Staff Bathroom

105 CMR 451.123	Maintenance: Floor paint damaged

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1050F

Front Inmate Bathroom

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 900F

Back Staff Bathroom

105 CMR 451.123*	Maintenance: Light shield missing

105 CMR 451.123*	Maintenance: Wall and floor paint damaged

105 CMR 451.123	Maintenance: Cold water control difficult to use

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 710F

Back Inmate Bathroom

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, excess water pressure

Paint Shop Trap and Bathroom	Locked at the time of inspection

Paint Shop Inmate Bathroom

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No paper towels at handwash sink

105 CMR 451.123	Maintenance: Eye wash station not maintained properly

105 CMR 451.123	Maintenance: Dead insects in eye-wash sink

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 660F

Building J

J Control Corridor

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light 	fixture not working properly

105 CMR 451.353	Interior Maintenance: Ceiling tiles water stained

Female Staff Bathroom

105 CMR 451.123	Maintenance: Floor damaged and no longer easily cleanable

105 CMR 451.123	Maintenance: Wall damaged and no longer easily cleanable

105 CMR 451.124*	Water Supply: Insufficient water supply in quantity and pressure at handwash sink

Male Staff Bathroom

105 CMR 451.123	Maintenance: Floor damaged and no longer easily cleanable

105 CMR 451.123	Maintenance: Wall damaged and no longer easily cleanable

Janitor’s Closet

No Violations Noted

Staff Kitchen and Dinning Room

Outside-Dry Storage

FC 6-501.111(B)	Maintenance and Operations; Pest Control: Arachnids and webs observed in dry 	storage closet

Back Door

FC 6-202.15(A)(2)	Design, Construction, and Installation; Functionality: Outer door not weather and 	vermin tight

Back Hallway Refrigerators and Freezer Units

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty, 	gasket dirty on 2nd refrigerator

Baking and Prep Room

FC 3-304.12(A)*	Preventing Contamination from Utensils: Service utensils handle stored below the 	food and container line, several Styrofoam bowls left in dry goods containers

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, dry goods containers lids damaged and do not close tightly

Refrigerator

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 450F

Staff Bathroom

No Violations Noted

Kitchen Area

Inmate Bathroom

No Violations Noted

Dry Storage Closet

FC 4-102.11(B)(2)	Materials for Construction and Repair; Multiuse: Unused single-service article not 	protected against contamination, plastic utensil boxes left open

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor paint 	damaged

2-Compartment Sink

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket, 	cloths store in a bucket of soap water

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, refrigerator gasket damaged

Dish Washing Area

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor tiles 	damaged

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, caulking dirty 	near rinse sink

Food Service Line

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Salad bar 	refrigerator temperature recorded at 580F

FC 4-204.112(A)	Design and Construction, Functionality: No functioning thermometer in salad bar 	refrigerator unit

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, dessert and salad bar cooler gaskets damaged

Ice Machine

FC 4-601.11(A)	Cleaning of Equipment and Utensils, Objective: Food contact surface dirty, interior 	surfaces of ice machine dirty

Dinning Room

FC 3-302.11(A)(4)	Preventing Food and Ingredient Contamination: Preventing cross contamination, 	several self-service food items not appropriately covered or protected by a sneeze 	guard

FC 6-202.15(A)(2)	Design, Construction, and Installation; Functionality: Outer door not weather and 	vermin tight

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, cardboard used to 	stabilize table

Janitor’s Closet

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not cleaned properly, vent dirty

Second Floor

Phase II Classification

Inmate Bathroom

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, sink fixture not functioning 	properly

Staff Bathroom

No Violations Noted

Inmate Bathroom-Waiting Area

Occupied at the time of inspection

Water Fountain

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, drain clogged

Slop Sink Room

No Violations Noted

Female Staff Bathroom

105 CMR 451.123	Maintenance: Wall damaged and no longer easily cleanable

Male Staff Bathroom

105 CMR 451.123	Maintenance: Unfinished wooden surface secured to wall

Staff Dinning Room

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 440F

105 CMR 451.350	Structural Maintenance: Wall damaged near microwave oven

J Housing Units

105 CMR 451.322*	Cell Size: Inadequate floor space in cells

Unit J1

Common Areas

105 CMR 451.353	Interior Maintenance: Wall paint damaged near cell # 18

Staff Bathroom

105 CMR 451.123	Maintenance: Wall paint damaged near toilet fixture

Staff Office

105 CMR 451.353*	Interior Maintenance: Vent cover missing

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty,	refrigerator gasket dirty

Slop Sink Room (1st Tier)

No Violations Noted

Slop Sink Room (3rd Tier)

No Violations Noted

Cells

105 CMR 451.353	Interior Maintenance: Sprinkler head cone not flush to wall in cell # 5

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 8

105 CMR 451.353	Interior Maintenance: Cone missing from sprinkler head in cell # 11

1st Tier Showers

105 CMR 451.123*	Maintenance: Soap scum on walls in shower # 2

105 CMR 451.123*	Maintenance: Shower curtain dirty in shower # 2

105 CMR 451.123	Maintenance: Shower # 1 out of order at the time of inspection

105 CMR 451.123	Maintenance: Ceiling dirty in shower # 2

105 CMR 451.123	Maintenance: Vent cover rusted in shower # 2

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation, vent painted over in shower # 2

2nd Tier Showers

105 CMR 451.123*	Maintenance: Floor tiles missing in all shower stalls

105 CMR 451.123	Maintenance: Vent rusted in both shower units

105 CMR 451.123	Maintenance: Soap scum on walls in shower # 1 and 2

105 CMR 451.123	Maintenance: Wall cover damaged in shower # 2

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation, vent painted over in all shower stalls

3rd Tier Showers

105 CMR 451.123*	Maintenance: Soap scum on walls in both showers stalls

105 CMR 451.123	Maintenance: Door frame paint damaged in both showers stalls

105 CMR 451.123	Maintenance: Shower floor need re-grouting in both showers stalls

105 CMR 451.123	Maintenance: Wall cover damaged in shower # 2

105 CMR 451.123	Maintenance: Floor tiles missing in shower # 2

105 CMR 451.140*	Adequate Ventilation: Inadequate ventilation, vent painted over in both showers stalls

Unit J2

Common Area

105 CMR 451.353	Interior Maintenance: Wall fan dirty near TV

105 CMR 451.353	Interior Maintenance: Water stains on wall near cell # 45

Staff Bathroom

105 CMR 451.126	Hot Water: Hot water temperature recorded at 980F

Slop Sink Room (1st Tier)

105 CMR 451.353	Interior Maintenance: Wall paint damaged

Slop Sink Room (3rd Tier)

No Violations Noted

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 4

105 CMR 451.353	Interior Maintenance: Sprinkler head not flush to wall in cell # 33

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 1, 3, 5, 7, 26, 30, and 41

1st Tier Showers

105 CMR 451.123*	Maintenance: Unfilled holes in wall cover at in shower # 1 and 2

105 CMR 451.123*	Maintenance: Soap scum on walls in shower # 1 and 2

105 CMR 451.123	Maintenance: Shower # 3 under repair at the time of inspection

2nd Tier Showers

105 CMR 451.123*	Maintenance: Unfilled holes in wall cover at in shower # 1 and 3

105 CMR 451.123*	Maintenance: Soap scum on walls in shower # 1 and 3

105 CMR 451.123*	Maintenance: Floor tiles damaged in all shower # 1

105 CMR 451.123*	Maintenance: Floor tiles missing in all shower # 3

105 CMR 451.123	Maintenance: Shower # 2 under repair at the time of inspection

3rd Tier Showers

105 CMR 451.123*	Maintenance: Soap scum on walls in both showers stalls

105 CMR 451.123*	Maintenance: Shower floor need re-grouting in both showers stalls

105 CMR 451.123	Maintenance: New wall finish peeling in shower stall

105 CMR 451.123	Maintenance: Shower curtain dirty

105 CMR 451.123	Maintenance: Floor tiles missing in shower stall

Unit J3

Staff Bathroom

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1060F

Slop Sink Room (1st Tier)

No Violations Noted

Slop Sink Room (3rd Tier)

105 CMR 451.130	Plumbing: Backflow preventer cap missing on slop sink

Water Fountain

No Violations Noted

Cells

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 1, 2, 3, 5, 7, 15, 22, and 38

1st Tier Showers

105 CMR 451.123	Maintenance: Soap scum on walls in shower stall # 1

105 CMR 451.123	Maintenance: Wall cover not sealed to floor in shower stall # 2

105 CMR 451.123	Maintenance: Floor unfinished in shower stall # 3

2nd Tier Showers

105 CMR 451.123*	Maintenance: Soap scum on walls in shower stall # 1, 2, and 3

105 CMR 451.123*	Maintenance: Wall cover damaged in shower stall # 3

105 CMR 451.123	Maintenance: Shower floor need re-grouting in shower stall # 1

3rd Tier Showers

105 CMR 451.123	Maintenance: Soap scum on walls in shower stall # 1 and 2

105 CMR 451.123	Maintenance: Wall cover damaged in shower # 1

105 CMR 451.123	Maintenance: Floor unfinished in shower stall # 2

Unit J4

Common Area

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, several light bulbs missing

105 CMR 451.353	Interior Maintenance: Light shield missing

Staff Room

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 460F

FC 4-501.13	Maintenance and Operation, Equipment: Microwave oven does not meet safety	standards, door damaged

Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling damaged

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 850F

Slop Sink

No Violations Noted

Cells

105 CMR 451.353	Interior Maintenance: Wall paint damaged in cell # 4

1st Tier Showers

105 CMR 451.123	Maintenance: Floor tiles damaged in shower stall # 1 and 2

105 CMR 451.123	Maintenance: Wall covering not secured properly in shower stall # 1 and 2

2nd Tier Showers	Occupied at the time of inspection

3rd Tier Showers

105 CMR 451.123	Maintenance: Unfilled holes in wall covering in shower stall # 1

105 CMR 451.123	Maintenance: Wall cover damaged in shower stall # 2

105 CMR 451.123	Maintenance: Vent cover rusted in shower stall # 2

105 CMR 451.123	Maintenance: Wall cover not sealed to floor properly in shower stall # 1

105 CMR 451.123	Maintenance: Floor tiles damaged in shower stall # 2

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head leaking in shower stall # 2

Unit J5

Common Area

105 CMR 451.353	Interior Maintenance: Water fountain dirty

105 CMR 451.353	Interior Maintenance: Water stains on wall near cell # 20

Staff Bathroom

No Violations Noted

Slop Sink Room

105 CMR 451.353	Interior Maintenance: Wet mop left in bucket

Cells

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 1, 4, 6, 7, 9, 13, 14, 26, 25, 37, 	and 38

1st Tier Showers

105 CMR 451.123*	Maintenance: Unfilled holes in wall covering in shower stall # 1, 2, and 3

105 CMR 451.123	Maintenance: Soap scum on walls in shower stall # 1, 2, and 3

105 CMR 451.123	Maintenance: Floor tiles damaged in shower stall # 3

105 CMR 451.123	Maintenance: Wall cover damaged in shower stall # 2

105 CMR 451.123	Maintenance: Wall covering not properly secured in shower stall # 1, 2, and 3

105 CMR 451.123	Maintenance: Vent cover missing in shower stall # 1

2nd Tier Showers

105 CMR 451.123*	Maintenance: Unfilled holes in wall covering in shower stall # 1 and 3

105 CMR 451.123*	Maintenance: Wall finish peeling in shower stall # 2

105 CMR 451.123	Maintenance: Light fixture not functioning properly in shower stall # 1

105 CMR 451.123	Maintenance: Wall cover damaged in shower stall # 1

105 CMR 451.123	Maintenance: Wall covering not properly secured in shower stall # 3

105 CMR 451.123	Maintenance: Shower floor need re-grouting in shower stall # 3

105 CMR 451.123	Maintenance: Floor unfinished in shower stall # 2

105 CMR 451.123	Maintenance: Soap scum on walls in shower # 3

3rd Tier Showers

105 CMR 451.123*	Maintenance: Wall cover damaged and unfilled holes in shower stall # 2

105 CMR 451.123	Maintenance: Vent cover missing in shower stall # 1

105 CMR 451.123	Maintenance: Floor unfinished in shower stall # 1

105 CMR 451.123	Maintenance: Wall finish peeling in shower stall # 1

105 CMR 451.123	Maintenance: Floor tiles missing in shower stall # 2

105 CMR 451.123	Maintenance: Vent dirty in shower stall # 2

105 CMR 451.123	Maintenance: Shower floor need re-grouting in shower stall # 2

Unit J6

Common Area

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, several light 	fixtures not working properly

105 CMR 451.350	Structural Maintenance: Floor damaged outside cell # 4

Staff Bathroom

No Violations Noted

Slop Sink Room (1st Tier)

105 CMR 451.353	Interior Maintenance: Wet mops not allowed to dry properly, wet mop left on floor

Slop Sink Room (3rd Tier)

No Violations Noted

Cells

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged in cell # 1, 4, 11, 29, 32, 35, and 36

1st Tier Showers

105 CMR 451.123*	Maintenance: Unfilled holes in wall covers in shower stall # 2 and 3

105 CMR 451.123	Maintenance: Soap scum on walls in shower stall # 2 and 3

105 CMR 451.123	Maintenance: Vent cover rusted in shower stall # 2 and 3

2nd Tier Showers

105 CMR 451.123*	Maintenance: Unfilled holes in wall covers in shower stall # 1, 2, and 3

105 CMR 451.123*	Maintenance: Wall cover damaged in shower stall # 1, 2, and 3

105 CMR 451.123*	Maintenance: Soap scum on walls in shower stall # 1

105 CMR 451.123	Maintenance: Shower floor need re-grouting in shower stall # 1 and 2

105 CMR 451.123	Maintenance: Floor tiles damaged in shower stall # 1 and 2

105 CMR 451.123	Maintenance: Ceiling paint damage outside shower stalls

105 CMR 451.123	Maintenance: Vent cover rusted in shower stall # 1, 2, and 3

3rd Tier Showers

105 CMR 451.123*	Maintenance: Soap scum on walls in both shower stalls

105 CMR 451.123*	Maintenance: Unfilled holes in wall covers in both shower stalls

105 CMR 451.123*	Maintenance: Wall cover damaged in both shower stalls

105 CMR 451.123	Maintenance: Floor tiles missing in shower stall # 1

Dorm J7

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm area

Bathroom

105 CMR 451.123	Maintenance: One night light not functioning properly

105 CMR 451.123	Maintenance: Vent cover missing

Shower Room

105 CMR 451.123*	Maintenance: Metal access door and vent covers rusted

105 CMR 451.123	Maintenance: Shower stall # R1 rusted

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head leaking in shower 	stall # R1

Health Service Unit

Hallway

No Violations Noted

Med Room C125B

No Violations Noted

Room C122

105 CMR 451.353	Interior Maintenance: Vent dirty

Nurses’ Control Area

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, several light 	fixtures not working properly

Waiting Rooms 102 to 104

No Violations Noted

Cell # 108

105 CMR 451.353	Interior Maintenance: Vent blocked

Cell # 110

No Violations Noted

Cell # 112

No Violations Noted

Shower Unit

105 CMR 451.123	Maintenance: Soap scum on walls in shower

105 CMR 451.123	Maintenance: Wall dirty

105 CMR 451.123	Maintenance: Vent rusted

105 CMR 451.123	Maintenance: Bench rusted

Slop Sink Room

No Violations Noted

Men’s Rom C107A

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1340F

Optometry Room C 108A

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1340F

Slop Sink Room C109A

No Violations Noted

Room C110A

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1330F

Trauma Room 2 C111A

No Violations Noted

Room C112A

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1350F

Room C114A

105 CMR 451.353	Interior Maintenance: Table unfinished and not easily cleanable

Exam Room C116A to C118A

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1350F in exam rooms

Staff Break Room C119A

No Violations Noted

Women’s Bathroom C 121

105 CMR 451.123	Maintenance: Hot water handle damaged

Back Storage

No Violations Noted

Exam Room C126

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1350F

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, cold water foot pedal missing

105 CMR 451.353	Interior Maintenance: Wall damaged

X-Ray Room C 127

No Violations Noted

Dental Exam Room C129 and C130

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 1350F

Building K

Staff Bathroom C-101

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 830F

Inmate Bathroom C-102

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 900F

105 CMR 451.123	Maintenance: Light shield filled with trash

Janitor’s Closet

105 CMR 451.353*	Interior Maintenance: Ceiling dirty

Protestant Chapel

No Violations Noted

Catholic Chapel

105 CMR 451.141	Screens: Screen damaged on window # 5 and 18

Islamic Chapel

No Violations Noted

Security Staff Room

No Violations Noted

Storage Room

No Violations Noted

Building L

Inmate Processing Common Area

No Violations Noted

Staff Break Room

FC 4-101.16	Materials for Construction and Repair; Multiuse: Sponges used in kitchen

Bathroom

105 CMR 451.123*	Maintenance: Handwash sinks dirty

105 CMR 451.123*	Maintenance: Ceiling paint damaged

105 CMR 451.123	Maintenance: Vent covers missing

105 CMR 451.123	Maintenance: Floor dirty

105 CMR 451.123	Maintenance: Tiles damaged

105 CMR 451.123	Maintenance: Light bulb and light shield missing

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 590F at sink # 1

105 CMR 451.126	Water Supply: No hot water supplied to handwash sink # 2

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, one toilet fixture missing

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet loose

Staff Bathroom

105 CMR 451.123*	Maintenance: Ceiling vent dirty

Dorms

Dorm Control

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty,	refrigerator gasket and door handles dirty

FC 4-602.12(B)	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

Control Bathroom

105 CMR 451.123	Maintenance: Ceiling vent dirty

L1 Dorm

Common Area

105 CMR 451.141	Screens: Two screens damaged

105 CMR 451.344	Illumination in Habitable Areas: Several light fixtures not working properly

105 CMR 451.350	Structural Maintenance: Two windows secured with tape

105 CMR 451.350	Structural Maintenance: Floor damaged

Bathroom L1-22	Occupied at the time of Inspection

Shower Room L1-23 A & B

105 CMR 451.123*	Maintenance: Soap scum on walls and floor in shower stalls

105 CMR 451.123	Maintenance: Ceiling and ceiling paint damaged in shower area

105 CMR 451.123	Maintenance: Possible mold growth on ceiling in shower stall # 1 and 2

105 CMR 451.123	Maintenance: Floor finish damaged in shower area

105 CMR 451.123	Maintenance: Wall vents dirty in shower stalls

105 CMR 451.123	Maintenance: Floor dirty in shower stalls

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head leaking in shower 	stall # 3 and handheld shower head in handicap equipped shower stall

Bathroom L1-24

No Violations Noted

Dorm L2

Common Area

105 CMR 451.141*	Screens: Several screen damaged

105 CMR 451.350*	Structural Maintenance: Ceiling water damaged in several areas

Bathroom L2-12

105 CMR 451.123*	Maintenance: Ceiling damaged

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, one urinal out of order

Shower Room L1-13 A&B

105 CMR 451.123	Maintenance: Soap scum on walls and floor in shower stalls

105 CMR 451.123	Maintenance: Light fixture not working properly in front of shower stall # 3 and 4

105 CMR 451.123	Maintenance: Ceiling and ceiling paint damaged in shower area

105 CMR 451.123	Maintenance: Wall vents dirty in shower stalls

Bathroom L1-14

105 CMR 451.123*	Maintenance: Floor dirty

105 CMR 451.123	Maintenance: One toilet fixture removed leaving an unfinished piece of wood to 		secure the opening

Dorm L3	Closed at the time of inspection

Modular Units

Lobby Area

No Violations Noted

Control Area

105 CMR 451.344	Illumination in Habitable Areas: One light fixture not working properly

105 CMR 451.350*	Structural Maintenance: Floor tiles and floor damaged

Staff Bathroom

105 CMR 451.123*	Maintenance: Floor tiles damaged and not easily cleanable

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1330F

A Side

Recreational Area

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

Bathroom

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1330F

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet loose on slop sink

Shower Room

105 CMR 451.123	Maintenance: Shower # 1 out of order-shower not in use at the time of inspection

105 CMR 451.123	Maintenance: Floor damaged in shower area

105 CMR 451.123	Maintenance: Vent not secured properly

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head leaking in shower 	stall # 3

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, shower head missing in shower 	stall # 4

A Dorm Rooms

1A

105 CMR 451.350*	Structural Maintenance: Floor tiles damaged

2A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

105 CMR 451.344	Illumination in Habitable Areas: One light fixture not working properly

3A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

4A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

5A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

6A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

7A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

8A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

9A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

10A

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

B Side

Recreational Area

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light

fixture not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

Bathroom

105 CMR 451.123*	Maintenance: Floor damaged

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1400F

Shower Room

105 CMR 451.123*	Maintenance: Floor damaged in shower area

105 CMR 451.123	Maintenance: Vent and speaker rusted in shower area

105 CMR 451.123	Maintenance: Ceiling damaged in shower area

105 CMR 451.123	Maintenance: Drain cover missing in shower stall # 1

105 CMR 451.123	Maintenance: Shower floor damaged in shower stall # 8

B Dorm Rooms

1B

105 CMR 451.350*	Structural Maintenance: Floor tiles damaged

2B

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

3B

105 CMR 451.344*	Illumination in Habitable Areas: Two light fixtures not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

4B

105 CMR 451.344*	Illumination in Habitable Areas: One light fixture not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

5B

105 CMR 451.344*	Illumination in Habitable Areas: Two light fixtures not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

105 CMR 451.353	Interior Maintenance: Light shield not secured properly

6B

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

7B

105 CMR 451.344*	Illumination in Habitable Areas: Two light fixtures not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

8B

105 CMR 451.344*	Illumination in Habitable Areas: One light fixture not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

9B

105 CMR 451.344	Illumination in Habitable Areas: Two light fixtures not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

10B

105 CMR 451.344	Illumination in Habitable Areas: Two light fixtures not working properly

105 CMR 451.350	Structural Maintenance: Floor tiles damaged

Outside Facility

Store House

Box 1

FC 6-202.11(A)	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, two light fixtures 	not functioning properly

Box 2

FC 6-202.11(A)*	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

Box 3	Used for storage at the time of inspection

Chemical Storage Room # 4

No Violations Noted

Slop Sink Room

105 CMR 451.353*	Interior Maintenance: Ceiling paint damaged

105 CMR 451.353	Interior Maintenance: Light shield not provided in a maintenance area

Men’s Room

105 CMR 451.123*	Maintenance: Light shield missing

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 550F

Freezer 5

FC 4-501.11(A)*	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, small amount of ice buildup in freezer unit

Cooler 6	Used for storage at the time of inspection

Cooler 7

FC 6-202.11(A)*	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, one light fixture 	not functioning properly

Staff Office

No Violations Noted

Staff Bathroom

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 590F

Inmate Break Room

No Violations Noted

Observations and Recommendations

- Hot water temperatures were not stable at the facility. On the first inspection day hot water temperature were well under the required minimum 1100F. During the second day of inspection the hot water temperatures were well in excess of the 1300F maximum temperature, reach up to 1800F in some housing units and 1500F in the lobby bathrooms. These excessive hot water temperatures are of particular concern as they present a scalding hazard to visitors, staff, and inmates

- Recommend storing paper towels in holders

- Recommend refrigerator units be calibrated and monitored closely to ensure proper cold holding temperatures are maintained throughout the facility

This facility does not comply with the Department’s Regulations cited above. In accordance with 105 CMR 451.404, please indicate next to each entry on the inspection report a plan of correction. Said plan of correction must be submitted within 10 days of receipt of this letter and should detail the specific steps that will be taken and the date of expected compliance. The plan of correction should be submitted to my attention, at the address listed above.

To review the specific regulatory requirements please visit our website at www.mass.gov/dph/dcs and click on "Community Sanitation Regulations" (available in both PDF and RTF formats).

To review the Food Establishment regulations please visit the Food Protection website at www.mass.gov/dph/fpp and click on “Food Protection Regulations”. Then under “Retail” click “105 CMR 590.000 - State Sanitary Code Chapter X – Minimum Sanitation Standards for Food Establishments” and “1999 Food Code”.

This inspection report is signed and certified under the pains and penalties of perjury.

Sincerely,

Lauren Molotnikov

Environmental Health Inspector, CSP, BEH

cc:	Suzanne K. Condon, Associate Commissioner, Director, BEH

Steven Hughes, Director, CSP, BEH

JudyAnn Bigby, MD, Secretary, Executive Office of Health and Human Services

Harold W. Clarke, Commissioner, DOC

George Frascarelli, EHSO

Cornelius Jones, EHSO

Concord Board of Health

Clerk, Massachusetts House of Representatives

Clerk, Massachusetts Senate

Mary Elizabeth Heffernan, EOPS